Palestinian National Authority

##### Ministry of Health

###### Procurement Department

Rehabilitation of Emergency Department

at Shohadaa Al Aqsa Hospital

Financed by: International Committee of the Red Cross ICRC

Tender No.: 56 /2013

TABLE OF CONTENT

Press Advertisement	3

Invitation for Tender	4

Special Conditions of Contract	5

General Conditions	8

Schedule of Requirements (BoQ)	22

Technical Specifications	51

Press Advertisement

Palestinian National Authority

Ministry of Health

General Directorate for Admin. &Finance

Procurement Department

Invitation for Tender no. ( 56 /2013)

to implement the Rehabilitation of Emergency Department at Shohadaa Al Aqsa Hospital

Funded by International Committee of the Red Cross

- Ministry of Health invites sealed tender from eligible contractors for implementing the project of Rehabilitation Emergency Department at Shohadaa Al Aqsa Hospitala Al Aqsaي000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000 Funded by the International Committee of the Red Cross (ICRC).

- Interested eligible contractors may obtain further information and inspect the tender documents at address below; from 8:00 am to 14:00 pm.

- A complete set of tender documents in English may be purchased by interested contractors on submission of a written application and upon payment of a non-refundable tender fee of only (300) NIS. The method of payment will be a check against receipt of voucher.

- Interested contractors should be registered at Contractors Union; classification should not be less than  second class in Construction and Electromechanical.

- Tender must be delivered to the address below by 12:00 p.m. on May 23, 2013.

- Pre-bid meeting will be held in Shohadaa Al Aqsa hospital at 10:00 am on Sunday May 19, 2013

- All prices are in NIS & VAT excluded. The awarded contractor should provide Zero VAT invoice duly stamped by MoF

- All tenders should be accompanied by a Bid Security equal to 5% of the total tender value from a local Bank, and should be issued in English and by the name of International Committee of the Red Cross (ICRC).

- Tender will be open immediately thereafter, in the presence of the contractors who choose to attend at the same address at which a contractor chooses to submit his tender at Thursday on 12:00 a.m. May 23, 2013

- Awarding contract will follow ICRC/MoH rules and not necessary the lowest price

- The successful contractor will pay advertisement fees.

- For more information, contractors could contact:

Procurement Department, 1st floor at the Administrative Companion

Ministry of Health, Administrative Companion

El Wehda Street, Remal,

Gaza,

Tele:08 -2824607,08-2838553,Fax: 08-2827634

- E-mail:  purch@moh.gov.ps

Invitation for Tender no. (56/2013)

Palestinian National Authority

Ministry of Health

General Directorate for Admin. &Finance

Procurement Department

Project of Rehabilitation of Emergency Department at Shohadaa Al Aqsa Hospital

Funded by International Committee of the Red Cross

- Ministry of Health invites sealed tender from eligible contractor for implementing the project of Rehabilitation Emergency Department at Shohadaa Al Aqsa Hospitala Al Aqsaي000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000 Funded by the International Committee of the Red Cross (ICRC).

- Interested eligible contractors may obtain further information and inspect the tender documents at address below; from 8:00 am to 14:00 pm.

- A complete set of tender documents in English may be purchased by interested contractors on submission of a written application and upon payment of a non-refundable tender fee of only (300) NIS. The method of payment will be a check against receipt of voucher.

- Interested contractors should be registered at Contractors Union; classification should not be less than second class in Construction and Electromechanical.

- Tender must be delivered to the address below by 12:00 p.m. on May 23, 2013.

- Pre-bid meeting will be held in Shohadaa Al Aqsa hospital at 10:00 am on Sunday May 19, 2013

- All prices are in NIS & VAT excluded. The awarded contractor should provide Zero VAT invoice duly stamped by MoF

- All tenders should be accompanied by a Bid Security equal to 5% of the total tender value from a local Bank, and should be issued in English and by the name of International Committee of the Red Cross (ICRC).

- Tender will be open immediately thereafter, in the presence of the contractors who choose to attend at the same address at which a contractor chooses to submit his tender at Thursday on 12:00 a.m. May 23, 2013

- Awarding contract will follow ICRC/MoH rules and not necessary the lowest price

- The successful contractor will pay advertisement fees.

- For more information, contractors could contact:

Procurement Department, 1st floor at the Administrative Companion

Ministry of Health, Administrative Companion

El Wehda Street, Remal,

Gaza,

Tele:08 -2824607,8-2838553,Fax: 08-2827634

- E-mail:  purch@moh.gov.ps

Section I.

Special Conditions of Contract

| 1. Tender Currency | The unit rates and prices shall be quote by the Contractor entirely in NIS. |
| --- | --- |
| 2. Tender Prices | The Contract shall be for the whole Works, as described in the schedule of requirement and technical specifications. |
| 3. Bid Validity | Tenders shall remain valid for the 90 days starting from the date of tender opening. |
| 4. Bid Security | All tenders should accompanied by a Bid Security equal to 5% of the total tender value, and should be issued from a local bank in English and by the name of International Committee of the Red Cross (ICRC). |
| 5. Performance Security | The successful Contractor should deliver to the Client a Performance Security for 10% of total value of the contract in the form of Bank Guarantee issued at the successful contractor's option by a local bank; and should be issued by the name of the International Committee of the Red Cross (ICRC) |
| 6. Maintenance Guarantee | Contractor should deliver Maintenance Guarantee by the end of the project 10% of the total amount of the contract, the guarantee should be issued from the approved banks ( please refer to ICRC contract) in the name of ICRC |
| 7. Signing contract | Within 7 days after receipt of the Letter of Acceptance, the successful Contractor shall sign the contract |
| 8. Time Control | The Contractor shall start his program for the Works within 7 days from the date of signing the contract and hand over the contract. |
| 9. Withdrawal from offers | If the winner contractor withdraws, he will loose the bid security guarantee attached with the offer |
| 10. Project period | Project period is 4 months starting from the date of sending the letter of Acceptance. |

Special Conditions of Contract

|  | 1.Advertisment 2.Invitation to Tender 3.Section I. Special Conditions of Contract 4.Section II GENERAL CONDITIONS 5.Section III Schedule of Requirements (BoQ) 6.Section IV Technical Specifications 7.Form of Contract |
| --- | --- |

# Section II

GENERAL CONDITIONS

INTERNATIONAL COMMITTEE OF THE RED CROSS

GENERAL CONDITIONS

CONTRACTS FOR WORK

1. DEFINITION.		11

2. OBLIGATION OF THE CONTRACTOR.		11

2.1. General		11

2.2. Certification		11

2.3. Compliance with professional standards		11

3. MATERIALS		12

4. SAMPLES		12

5. CONCEALED WORKS		12

6. INFORMATION		13

6.1. Right of inspection		13

6.2. Site meeting reports		13

6.3. Final report		13

7. MODIFICATIONS: ADDITIONAL AND / OR ELIMINATED WORKS		13

7.1. Principles		13

7.2. Price		13

8. SUBCONTRACTING		14

8.1. Principle		14

8.2. Payment of Subcontractors		14

8.3. Obligations of the Subcontractors		15

9. ASSIGNMENT		15

10. ACCEPTANCE PROCEDURE / GUARANTEE FOR DEFECTS		15

10.1. Notice of completion of work		15

10.2. Defects		15

10.3. Repairs		16

10.4. Provisional acceptance		16

11. FINAL ACCEPTANCE / WARRENTY		16

12. FIXED PRICE CONTRACTS		16

13. PENALITES		16

14. INSURANCE		17

15. PLEDGE OF DISCRETION / ICRC NAME AND LOGO		17

16. INTELLECTUAL PROPERTY RIGHTS		17

17. PAYMENT		17

18. CANCELLATION OF THE CONTRACT		18

18.1. In general		18

18.2. For exceeding of estimates		18

18.3. Consequences of the cancellation		18

19. CANCELLATION AGAINST INDEMNIFICATION		18

20. FORCE MAJEURE		19

21. RESPECT FOR HUMANITARIAN VALUES		19

22. WORKING CONDITIONS AND CHILD LABOUR		19

23. RESPECT FOR THE LAW		19

24. MINES AND OTHER WEAPONS		20

25. SECURITY WARNING / DISCHARGE FROM LIABILITY		20

26. MODIFICATIONS OF GENERAL CONDITIONS AND / OR CONTRACT		20

27. ENFORCEABILITY / VALIDITY		20

28. ARBITRATION		20

29. IMMUNITY		21

# DEFINITION

A contract for work is an agreement whereby the Contractor obligates himself to produce a work, and the Client to pay the price.

# OBLIGATION OF THE CONTRACTOR

## General

The Contractor shall protect the interests of the Client and perform the work and have them performed in accordance with the documents referred to in the contract and shall draw up any other supplementary or detailed plans which may be necessary for the performance of the contract.

He is obligated to carry out the work personally or to have it carried out under his personal direction.

## Certification

The Contractor certifies that it has:

- Visited and inspected the site and location of the works

- Taken full and entire note of the plans and descriptions

- Verified the plans and the preliminary bills of quantities

- Asked for all and any necessary or relevant information, pertaining to and for the calculation of its all-included price.

## Compliance with professional standards

The Contractor must apply the same care and knowledge one may expect from a professional and diligent contractor in the same line of work taking all necessary precautions, respecting his contractual obligations and applying state of the art rules.

In the absence of an agreement to the contrary or custom, he shall himself provide for such accessories, instruments and equipment as shall be necessary for the carrying out of the work.

The Client has the right to reject any material, equipment or work performed not meeting the standards as stated in the contract.

In particular the Contractor shall:

2.3.1	Ensure a high quality level of work in accordance with the national standards for civil and mechanical work. The Contractor will have the work executed only by an experienced labour force.

2.3.2	Ensure a close supervision of the work quality with a qualified engineer as supervisor where necessary during the entire duration of the work.

2.3.3	Bear full responsibility for implementing all safety procedures in compliance with all applicable safety and labour laws, and bear full responsibility for any accidents arising from the normal execution of the work.

2.3.4	Ensure that local services are disrupted for the minimum duration of time during the work, and coordinate with the relevant authorities in order to warn any potentially affected people of any necessary shutdowns.

2.3.5	Clean the site and take good care of it during the work. All debris, garbage, waste materials and construction equipment, used during the project must be taken out of the work site on termination or completion of the contract.

2.3.6	Keep, of its own volition, the Client informed of unforeseen or significant occurrences or difficulties, particularly in the event of a delay in the work and supply the Client with the information the latter requests.

# MATERIALS

To the extent that the Contractor has undertaken to supply the material, he is liable to the Client for the quality and is bound by a warranty in the same manner as a seller.

If, during the carrying out of the work, defects become evident in the material supplied by the principal or with regard to the designated construction site, or other conditions develop which endanger a due and timely carrying out of the work, the Contractor shall without delay notify the Client thereof, otherwise he bears the adverse consequences himself.

# SAMPLES

The Contractor shall without additional charge whenever requested by the Client supply samples for selection or quality control purposes. Such supply and the selection by the Client shall be effected in good time to ensure that no delay results.

4.1	All workshop or laboratory tests will be at the Contractor's expenses. The Contractor will provide the results for acceptance by the Client within three days after the testing.

4.2	The Contractor must submit any pumping equipment for testing one week prior to its use on-site to an agreed workshop specified by the Client.

# CONCEALED WORKS

All parts of the work that will be hidden from view are to be inspected by the Client prior to their covering. At the Client's request, the Contractor must uncover any hidden work for further inspection or testing.

# INFORMATION

## Right of inspection

The Client shall have the right to inspect the progress and performance of the work, as well as its quality and that of the materials being used.

The Client's right of inspection shall not in any way relieve the Contractor of its responsibilities for the performance of the work.

## Site meeting reports

The Contractor shall hold regular site meetings, to which the Client shall be invited. In any event, the minutes of the meetings shall be sent to the Client.

## Final report

When the work is concluded, the Contractor shall deliver to the Client, free of charge, the file certified by the Contractor containing the operating instructions, together with all the necessary plans, duly updated and certified, where necessary, by the Contractor's architects and engineers. These shall include in particular:

- Paper of electronic drawings of the plans implemented

- Diagrams and operating instructions for all installations

- A list of the subcontractors and their contact details.

# MODIFICATIONS: ADDITIONAL AND / OR ELIMINATED WORKS

## Principles

If the Client wishes to change, amend or improve the work it must provide the Contractor with a written request in good time.

To determine the feasibility, the increase or reduction in prices and the impact on delivery dates, the Contractor will have a period of fifteen days from receipt of the request to draw up a detailed written offer showing whatever effect the modification might have on the work.

The desired modification will be carried out and paid for only if the Client has accepted the conditions, delivery dates and impacts on the initial work in writing.

If the Contractor refuses the modifications for feasibility or deadline reasons in spite of the Client assuming responsibility for all consequences in connection with the modifications, the Client may have the modifications executed by a third party.

## Price

The additional work necessitated by the modifications or improvements referred to above will be calculated on the basis of the unit prices taken into consideration for fixing the price of the work, including any discounts.

Work, which will be eliminated, will be deducted from the price, on the basis of the unit prices used when calculating and fixing the price of the work, excluding any discounts. Compensation has to be paid to the Contractor for any loss of earnings due to this elimination.

If the parties cannot agree on the cost of any additional work, the Client shall have the right to invite competing tenders and, if necessary, impose the resulting prices on the Contractor.

# SUBCONTRACTING

## Principle

The Contractor may sign contracts for work with tradesmen, contractors and contractors (hereinafter referred to as "Subcontractors"), as well as with any other agents taking part in the work.

The Contractor will make such contracts in its own name and for its own account. Vis-à-vis the Subcontractors and agents, the Contractor shall have all the rights and prerogatives of a Client. Towards the Client, the Contractor remains entirely liable for any work executed by such third parties as if he had executed the work himself.

The Contractor does not have the right to hire any employee of a relevant ministerial authorities, ministerial sub-directorates, or of relevant municipal agencies, nor any member of any governmental agency or institution.

The Contractor must provide the Client with the business name of any Subcontractor or agent to whom it is intended to award a job so as to enable the Client, where applicable, to state its reservations. The Client may object to them only on reasonable grounds.

The fact that the Contractor awards a job to a subcontractor proposed but not imposed by the Client shall not relieve the Contractor of any of its obligations, responsibilities or liabilities.

## Payment of Subcontractors

The Contractor undertakes

8.2.1	to use the Client payments only for invoices in relation to the construction of the work

8.2.2	to pay the Subcontractors punctually for the amounts due to them

8.2.3	to produce a statement of its payments to the Subcontractor at any time upon simple request.

To permit compliance with this obligation to be checked, the Contractor may be requested to open a special account with a banking institution designated by the Client.

The Client shall have the right to make full and final payment directly to the Subcontractor of the amount agreed between the Contractor and the Subcontractor. The amount thus paid will be charged by the Client to the remuneration owed by him to the Contractor. In the event of a dispute over an amount between the Contractor and the Subcontractor, the Client shall be entitled to have the amount placed on deposit with the effect of full and final settlement vis-à-vis the Contractor.

## Obligations of the Subcontractors

The Contractor will ensure that the following provisions are included in all contracts concluded with its subcontractors:

8.3.1 	The Subcontractor undertakes to carry out the work personally using its own resources such that, as a rule, further subcontracting is excluded.

8.3.2	The Subcontractor guarantees the same high quality of work as the Contractor, respecting laws and professional standards one might expect from a professional in the same line of  work.

8.3.3 	Exceptionally, the Subcontractor may be permitted by the Contractor to sub-subcontract a part of the work, on condition that written authorisation has been sought and granted by the Client.

8.3.4 	If, by way of exception, the authorization to sub-subcontract is granted, the Subcontractor shall remain as liable for the work of its Sub-Subcontractor as it is for its own.

# ASSIGNMENT

The Contractor may not assign all or any part of its rights and obligations under this contract to a third party, save with the written consent of the Client given expressly and in advance.

# ACCEPTANCE PROCEDURE / GUARANTEE FOR DEFECTS

## Notice of completion of work

The Contractor will inform the Client that the work has been completed and call a meeting for the examination and provisional acceptance of the work. The parties will draw up a report noting the result of the examination.

In any case, the Client shall, as soon as appropriate according to usual business practice, examine the quality of the work and immediately notify the Contractor of defects, if any.

## Defects

If defects are noted, the Client will set a time limit for the Contractor to remedy them. A defect is the absence of a quality promised by the Contractor or which the Client was entitled to expect under the rules of good faith.

If the defects are not remedied within the said time limit, the Client may:

- either make a corresponding reduction of the price

- or have the defects remedied by a third party at the Contractor's costs and deduct the costs from the letter of guarantee.

Where the work suffers from defects which are so substantial, or deviates from the contractual specifications to such an extent, that it is unusable for the Client or that its acceptance cannot reasonably be expected of him, the Client is entitled to refuse acceptance and to cancel the contract (art. 18.3 "Consequences of cancellation" applies).

## Repairs

The defects repaired must be accepted in accordance with the above procedure.

## Provisional acceptance

- If the completion of work report does not note any defects, or

- If the Client has accepted the work in the completion of work report or by omitting to examine and notify defects in due time, or

- If a report confirms that the repairs have been properly carried out,

the work will be provisionally accepted.

# FINAL ACCEPTANCE / WARRENTY

Final acceptance of the work will be pronounced one year after the provisional acceptence (Warranty Period), provided that no defect is discovered. The discovery of minor faults will not prevent final acceptance but will give rise to a new notice of completion for the part of the work concerned. The discovery of major faults will prevent final acceptance and will give rise to a new notice of completion.

The warranty does not cover damages due to misuse, user's negligence, wear and tear or any other damages due to risks to be borne by the Client according to normal business practices.

Irrespective of final acceptance, the Contractor shall remain liable for a period of five years for defects which during the reception and proper examination were not perceptible or were intentionally concealed by the Contractor.

# FIXED PRICE CONTRACTS

If the compensation has been precisely stipulated in advance (fixed price), the Contractor is obligated to complete the work for this sum and may not claim an increase even if he had more labour or larger expenditures than had been foreseen.

If, however, extraordinary circumstances which could not have been foreseen or which were excluded from the assumptions made by both parties, impede the completion or render it exceedingly difficult, the judge may, in his discretion, authorize an increase of the price or dissolution of the contract.

The principal shall also pay the full price if the completion of the work has caused less labour than had been foreseen.

# PENALITES

The penalty clause, if any, will be imposed for late completion of the contract unless due to Force Majeure without prejudice to other measures stipulated in the contract such as early termination. Nevertheless, the Contactor must inform the Client immediately in the case of possible delays or Force Majeure in order to enable the Client to take any appropriate measures.

The Client has the right to deduct the penalty without further process either from any outstanding bills or from the retention to be returned or use it to compensate any claims the Contractor might have against him.

Even if the penalty clause is applied, the Client may still choose to cancel the contract according to these General Conditions.

# INSURANCE

Nothing in the parties' relations shall be construed as an employment relationship. The Contractor therefore bears sole responsibility for insurance (old-age, invalidity, unemployment, accident, sickness, loss of earnings, third-party liability), for which he shall take out adequate coverage for himself and his employees.

# PLEDGE OF DISCRETION / ICRC NAME AND LOGO

The objective of the ICRC is to provide protection and assistance for victims of war, civil war or internal disturbances and for other victims on whose behalf the ICRC is called upon to take action. To attain this objective as effectively as possible, the ICRC must at all times enjoy the confidence of governments and of the victims.

This confidence is largely based on the neutrality of the ICRC and on the discretion with which it conducts its activities and, in particular, on its undertaking that any body active for the ICRC will never disclose what he sees or learns while working for the ICRC.

Accordingly, anybody active for the ICRC therefore undertakes to observe the utmost discretion concerning matters with which he shall be called upon to deal or which may come to his knowledge and to consider himself bound by professional secrecy in this regard.

This duty shall remain in effect even after the contract has ended.

The use of the name and / or logo of the ICRC in any way is prohibited unless expressly authorised in writing in advance.

# INTELLECTUAL PROPERTY RIGHTS

The Contractor herewith automatically cedes to the ICRC all transferable intellectual property rights to the results of his work for the ICRC. These rights include, but are not limited to, the exclusive right to use, publish, sell, modify or distribute any material prepared for or on behalf of the ICRC.

# PAYMENT

The conformity of the scheduled payments to the real progress must be certified by the Contractor. This certification must be attached to each invoice so that the Client can verify the situation.

The time limit for payment is 30 days from the date of receipt of the invoice from the Contractor.

The Client may require that the payment be made into a specicial construction account with a specific bank, so as to ensure that the money is properly used and, particularly that payment is received by the various subcontractors.

By way of guarantee, the Client may retain an agreed percentage of the value of each invoice.

In the event of unjustified delay by the Client in paying an invoice, the Client will be liable to pay the Contractor the National Bank default interest rate with effect from the date of formal notice by the Contractor, as well as any bank loan charges to the Contractor.

No adjustment to the price of the Contract will be made due to variations of the exchange rates.

# CANCELLATION OF THE CONTRACT

## In general

If, during the carrying out of the work, the performance of either party can definitely be anticipated to be faulty or otherwise in breach of the contract, then the innocent party may set an appropriate time limit for a remedy, with the warning that, in the event of the other party's failure to perform the correction or continuation of the work, the contract may be cancelled. The Client has also the choice to give the work to a third party at the Contractor's risk and cost.

Either party may cancel this contract if the other party becomes insolvent.

## For exceeding of estimates

If an approximate estimate of the price or the time frame for the completion of the work agreed upon with the Contractor is exceeded disproportionately without interference of the Client, the latter is entitled, during as well as after completion of the work, to cancel the contract.

## Consequences of the cancellation

In the event that the contract is terminated, the parties return to each other what they have already received. If the work or part of it can not be returned and if it is of value to the Client, the later shall pay an equitable compensation. The same applies where constructions on real property could only be removed at a disproportionate disadvantage for the Contractor.

Claims for damages and / or interests are reserved.

# CANCELLATION AGAINST INDEMNIFICATION

As long as the work is incomplete, the Client may withdraw at any time from the contract, against compensation for the work already performed and against full indemnification of the Contractor's loss of earnings.

# FORCE MAJEURE

Neither of the parties shall be held liable for a delay or any other failure to perform brought about by unforeseeable natural disaster, civilian unrest, strike or government restriction / constraint independent of the will of the party invoking it, provided that said party:

- informs the other party immediately of the existence of the cause and potential delay, and

- does all it can to discharge its obligations in spite of that cause.

If the cause persists for seven days, either of the parties may cancel the contract by informing the other party in writing (art. 18.3 "Consequences of cancellation" applies).

# RESPECT FOR HUMANITARIAN VALUES

For the duration of the contract, the undersigned may according to the circumstances be considered “close” to the ICRC. His acts and/or behaviour may reflect on the image and/or the reputation of the ICRC. He therefore undertakes to comply with the essence of the relevant ICRC rules of conduct and to adopt an attitude compatible with the purely humanitarian nature of the organization’s work, in accordance with the attached “Rules to be observed by individuals who work for the ICRC”. This does not mean, however, that the undersigned, who remains self-employed, thus establishes an employment relationship with the ICRC.  The latter may cancel the contract if the undersigned does not respect these rules and/or if ICRC's association with the undersigned is detrimental to ICRC's actions or reputation (art. 18.3 "Consequences of cancellation" applies).

# WORKING CONDITIONS AND CHILD LABOUR

22.1	By virtue of the Universal Declaration of Human Rights, the Convention on the Rights of the Child and the ILO's Declaration on Fundamental Principles and Rights at Work, the Contractor must respect the following:

- prohibition on the use of child labour;

- prohibition on the use of forced labour;

- national laws regarding hygiene, safety and labour rights.

22.2	The application of these principles shall be based on the laws of the country in which the work is located.

22.3	Should those laws fail to be observed by the Contractor and / or its Subcontractors or suppliers, the Client may make recommendations. If these are not followed, the Client shall be entitled to suspend or cancel the contract (art. 18.3 "Consequences of cancellation" applies).

# RESPECT FOR THE LAW

The Contractor undertakes to comply with the law. Should he nevertheless fail to do so, the Client shall be entitled – depending on the seriousness of the breaches and the significance which he judges those breaches to have had regarding the ICRC's operations – to cancel the contract (art. 18.3 "Consequences of cancellation" applies).

# MINES AND OTHER WEAPONS

The Contractor hereby certifies not to be involved in any manner whatsoever in the transport, sale and / or production of mines or any other weapons. Should the Contractor make a false certification in this respect, the Client shall be entitled to cancel the contract with immediate effect (art. 18.3 "Consequences of cancellation" applies).

# SECURITY WARNING / DISCHARGE FROM LIABILITY

The nature of the ICRC’s work and of armed conflicts can make working for the ICRC highly dangerous. Risks include injury, kidnapping and death. Contractors must be aware of these risks and know that in case of a kidnapping it is ICRC policy not to pay any ransom and that no insurance has been concluded for that purpose. The Contractor confirms that he has been informed of and accepts these risks. In any case, the ICRC’s and its employees' liability is expressly excluded.

The Contractor must be thoroughly familiar with any specific instructions that apply at the delegation and comply with them at all times.

# MODIFICATIONS OF GENERAL CONDITIONS AND / OR CONTRACT

No modification of the clauses of these General Conditions or of the Client's standard contract may be effected without the express written agreement of both parties.

# ENFORCEABILITY / VALIDITY

Any provision of the contract prohibited by or unlawful or unenforceable under any applicable law shall to the extent required by such law be ineffective without modifying the remaining provisions of the contract.

Where however the provisions of any such applicable law may be waived they are hereby waived by the parties hereto to the full extent permitted by such law to the end that the contract shall be a valid and binding agreement enforceable in accordance with its terms.

# ARBITRATION

If the contract provides for arbitration, any dispute, controversy or claim arising out of or in relation to the contract, including the validity, invalidity, breach or termination thereof, shall be finally and exclusively settled by arbitration in accordance with the UNCITRAL (United Nations Commission on International Trade Law) arbitration rules in force on the date when the Notice of arbitration is submitted in accordance with these Rules.

Appointing authority shall be the Chamber of Commerce and Industry of Geneva, Switzerland.

The arbitral proceedings shall be conducted in English.

# IMMUNITY

Nothing in these General Conditions and/or in the contract shall be directly or indirectly interpreted as a waiver on the part of the ICRC of its privileges and immunities as an international organization.

Read and accepted:

Place and date:______________________	Signature:	________________________

# Section III

Schedule of Requirements (BoQ)

| GRAND SUMMARY |  |  |
| --- | --- | --- |
| The contract amount shall be considered the ceiling not to be exceeded. The Client will pay the Contract Amount only; it is deemed to include all expenses. |  |  |
| Bill No.1 (Demolition and dismantling item) |  | NIS |
| Bill No. 2 (Masonry Works) |  | NIS |
| Bill No.3 (Carpentry and Joinery Works ) |  | NIS |
| Bill No.4 (Aluminum and Metal works) |  | NIS |
| Bill No. 5 (Plastering Works) |  | NIS |
| Bill No.6 (Painting Work) |  | NIS |
| Bill No.7(Tiling And Marble Work) |  | NIS |
| Bill No.8 (Proofing Works) |  | NIS |
| Bill No.9 (Mechanical Works) |  | NIS |
| Bill No.10 (Electrical Works) |  | NIS |
| Grand Total |  | NIS |
| Contract Price In Words |  |  |
| Contractor's Company Name |  |  |
| Contractor Representative Name |  |  |
| Contractor Representative Signature |  |  |
| Stamp |  |  |
| Date |  |  |

| Bill No. 1 (Demolition and dismantling item) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item No. | Description | Unit | Qty | Rate NIS | Amount NIS |
| Notes: | 1-Prices include a provision for hindrance due to current situations. 2-Prices include safety provisions . 3-Prices include the procedures and requirements as specified in the technical specifications and drawings. 4-Prices include all required Engineering tests. 5-Prices include all the required to complete the work in accordance with engineer's instructions. 6-Prices include all direct and indirect works and expenses required for the completion of the coming items are included in the unit prices. All quantities are measured from drawings. |  |  |  |  |
| 1.01 | 1- Dismantle wooden doors complete with frames and all accessories and keep it in a good condition to deliver it to the engineering &maintenance department or according to the supervisor engineer instructions. 2- Dismantle washing basins and w.cs complete with all accessories , keep it in a good condition and deliver it to the engineering & maintenance department or according to the supervisor engineer instructions. | L.S | 1 |  |  |
|  | 3- dismantle existing false ceiling and partitions keep it in a good condition and deliver it to the engineering & maintenance department or according to the supervisor engineer instruction |  |  |  |  |
|  | 4- dismantle scrubbing basins complete with accessories keep it in a good condition and deliver it to the engineering & maintenance department or according to the supervisor engineer instruction |  |  |  |  |
|  | 5- Remove sewage & water supply system |  |  |  |  |
|  | 6- Removing all tiles in floors & floors |  |  |  |  |
|  | 7- Removing all needed walls |  |  |  |  |
|  | 8- Removing all pvc floors in operation department |  |  |  |  |
|  | Delivering any suitable materials that be dismantled and not needed in the location for the engineering & maintenance department , or to the location that approved from the supervisor engineer . |  |  |  |  |
|  | Cart away the depressed material and all required as per engineering instructions. |  |  |  |  |
|  | Total Bill No.1 (Carried to summary) |  |  |  |  |
| Note: All relevant specifications requirements, drawings, and details are to be taken into account. |  |  |  |  |  |

| Bill No. 2 (Masonry Works) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Item No. | Description | Unit | Qty | Rate NIS | Amount NIS |  |
|  | The items (masonry works) include the supplying and testing of all required materials (concrete hollow block , cement, morter, casting concrete between Walls and Columns and R.C. Walls of width not less than 10cm. All in accordance with the specification, conditions of contract, drawings and instructions of the Engineer. |  |  |  |  |  |
| 2.01 | Supply and build hollow blocks 40*10*20 cm with compressive strength 35 kg/cm2 for internal walls, the contractor should: 1.Spray the blocks with water before and after built for at least two days 2. The contractor should consider the vertical and horizontal leveling 3. The mortar should be used within 30 min after mix 4. Close all openings between the walls & ceiling 5. Payment will be according to measured executing works 6. the item includes casting rein. concrete between columns and walls (20 cm ave. width) with steel reinforcement 4T 8 mm and steel sterupsT6 mm every 20 cm. the item includes supply and cast reinforced sills and lintels 20cm height with steel reinforcement 4T 8 mm and steel sterupsT6 mm every 20 cm. the item includes also includes the examination of the block as well as of cement mortar (the ratios must be 1:3 cement and sand.) | m2 | 560 |  |  |  |
|  | Total Bill No.2 (Carried to summary) |  |  |  |  |  |
| Note: All relevant specifications requirements, drawings, and details are to be taken into account. |  |  |  |  |  |  |

| Bill No. 3 (Carpentry and Joinery Works ) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item No. | Description | Unit | Qty | Rate NIS | Amount NIS |
|  | The item (carpentry and joinery works) include supplying and testing carpentry from soft wood class A, unless otherwise said ,the leaf should be surrounded by edge of hard wood edge (ZAN) 5*2.5 cm , and covered by laminated plastic sheet (Formica) 0.8mm . the item including frame cover mould ,architrave, Middle and bottom kick plates (Norista 1mm thick), hardware locked type wally (SWITCH) or equivalent approved, required glasses of 6mm thickness, and all other needed fittings, according to specifications, drawings and engineer's instructions. The price includes the prime painting before starting plastering and two coats of oil painting (Approved type first class), unless otherwise said, the color according to the engineer. - Galvanized steel frame and all the necessary installation and completion of the work duly instructed the supervising engineer. -Frame should be established according to the instructions supervising engineer -The width of frame by taking into account the thickness of the wall thickness of the plastering or ceramic on both sides - The contractor should submit sample for approval before starting. |  |  |  |  |
|  | [door opening size is a structural opening size] The lowest part of the door( under locks) shall be solid wood and the upper part shall be 50% solid & 50% void. |  |  |  |  |
| 3.01 | Supply, fix and paint flushed external wooden doors type Dw1, overall size 200x230cm swing double leaf .the price include the lower part 1.00m height is solid hard wood , 40*60* 0.6 cm glazed opening in each leaf | No. | 1 |  |  |
| 3.02 | Ditto, type Dw2 but swing door size 170*230cm , the lower part is soft solid wood | No. | 3 |  |  |
|  | Ditto, type Dw2* but hinged door size 170*230cm | No. | 1 |  |  |
| 3.03 | Ditto, type Dw3 for X-Ray Room but hinged door size 150*230cm , the lower part is solid soft wood. The price include 2mm lead sheets from both sides | No. | 1 |  |  |
| 3.04 | Supply, fix and paint flushed internal wooden doors type Dw4, overall size 90x230cm hinged leaf. | No. | 13 |  |  |
| 3.05 | Ditto but Dw5 with lead sheets from both sides | No. | 1 |  |  |
| 3.06 | Supply, fix and paint wooden hinged door, type Dw6 door size 150*230cm | No. | 2 |  |  |
| 3.07 | Supply, fix and paint flushed internal wooden doors type Dw7, overall size 100x220cm hinged leaf special for handicapped. | No. | 1 |  |  |
| 3.08 | Supply, fix and paint flushed internal wooden doors type Dw8, overall size 80x220cm hinged leaf for bath rooms | No. | 2 |  |  |
| 3.09 | Supply and install covering wooden ( soft wood first class) for protection 17 x 2 cm according to drawings and engineer instruction including fasteners and painting of warnish type according to the drawings, details and Engineer instructions. The contractor should submit shop drawings for approval before starting the works | L.M | 180 |  |  |
| 3.10 | Supply, fix and paint wood voids 4x4cm by screws and plywood sheet 4mm thick screwed to walls by bolts for covering the walls of x-ray rooms the price include wooden pieces 4*4 cm – to make voids- , all needed materials & fittings according to engineer instructions and drawings. | m2 | 50 |  |  |
|  | Total Bill No.3 (Carried to summary) |  |  |  |  |
| Note: All relevant specifications requirements, drawings, and details are to be taken into account. |  |  |  |  |  |

| Bill No.4 (Aluminum and Metal works) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item No. | Description | Unit | Qty | Rate NIS | Amount NIS |
|  | The items below (Aluminum and metal works) include supplying and fixing anodized coated colored aluminum windows type E.A. 4500 for hinged windows and for fixed windows -upper partitions ),and all requirements as frame ,clear glass 4mm thick for windows), ironmongery, accessories and hardware ,supplying and installing window frame, closing openings with (bostec) from inside and outside as per specifications, drawings and Engineer's instructions. The steel works including painting with priming and two layers of oil paint, unless otherwise said, according to the Engineer. The contractor should submit sample and shop drawing for approval by the Engineer before starting. The material used must have a valid quality certification from the Palestinian Institute for Standards and Measurements and must be tested in licensed Lab. |  |  |  |  |
|  | ALUMINUM WINDOWS |  |  |  |  |
| 4.01 | Supply and fix aluminum window : *Type W1 overall size 220x120cm, profile 7000, fixed window clear glass 4mm thick, with all ironmongery, hardware and all required accessories. the item includes supply and lay local marble first class (Khalili) 3cm thick for window sill laid on 2.5cm thick mortar bed and three semicircular opening according to drawings & Engineering instructions . | No. | 1 |  |  |
| 4.02 | Ditto but Type W2 overall size 80x120cm with one semicircular open & steel protection | No. | 1 |  |  |
| 4.03 | Supply and fix aluminum window : *Type W3 overall size160x80cm, profile 7000, sliding window clear glass 4mm thick, with all ironmongery, hardware and all required accessories. the item includes supply and lay local marble first class (Khalili) 3cm thick for window sill laid on 2.5cm thick mortar according to drawings & Engineering instructions . | No. | 1 |  |  |
| 4.04 | Ditto but Type W4 overall size 80x120cm | No. | 1 |  |  |
| 4.05 | Supply and fix aluminum door : *TypeDal1 overall size 100x220cm, consists of one leaf profile 2000 sliding, clear glass 6mm thick, according to engineer instructions and drawing including all required accessories and glass 6mm thickness, as per drawings and according to the Engineer's approval. The price include locked type Wally switch, or AE Aluminum hands and hinges. | No. | 2 |  |  |
| 4.06 | Ditto but Type Dal2 overall size 80x220cm consists of one sliding leaf profile 2000 sliding, the price include fiber sheets ,according to engineer instructions and drawing i | No. | 2 |  |  |
| 4.07 | Supply and fix aluminum partitions: consists of fixed frames profile 4*6.5cm ,with clear glass 6mm thick as shown in drawings , with all ironmongery, hardware and all required accessories. | m2 | 35 |  |  |
|  | Total Bill No.4 (Carried to summary) |  |  |  |  |
| Note: All relevant specifications requirements, drawings, and details are to be taken into account. |  |  |  |  |  |

| Bill No. 5 (Plastering Works) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item No. | Description | Unit | Qty | Rate NIS | Amount NIS |
|  | All works should comply to engineering specifications, supervision engineer approval, and the prices includes the following: 1. Supply and install all required material (cement, sand, expanded metal lath, corners from galvanized steel mesh , angle beads, and cloth mesh between plastering and blocks etc…) and workmanship (installation of scaffolding and dismantling etc …..) 2. Fill all spaces with cement mortar around electrical and water installation. The contractor should also clean the surface and remove all objects before plastering, the contractor also should spray the surface for three days 3. Any cracks between the columns should be treated with Sikaplix 4. The first layer of the plastering should be in one direction and should be leveled 5. Payment is according to measure quantities |  |  |  |  |
| 5.01 | Supply and execute internal plastering 15mm thick (three coats) for new walls and the areas of ceiling and walls that will be plastered after demolishing some walls , soffits, side of columns, jambs and reveals of openings, window sills, …etc. including galvanized metal lath angles where needed, edges and chicken wire at the intersection of concrete and block works, pipes. The price include maintenance the old walls where needed | M2 | 1050 |  |  |
|  | Total Bill No.5 (Carried to summary) |  |  |  |  |
| Note: All relevant specifications requirements, drawings, and details are to be taken into account. |  |  |  |  |  |

| Bill No.6 (Painting Work) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item No. | Description | Unit | Qty | Rate NIS | Amount NIS |
|  | The items( Painting works) include the supplying of all required material (paints, putty,….,) approved from Authorized institutions and workmanship. The walls and other elements to be painted should be cleaned. The color is according to the Engineer approval. All according to the specifications, drawings, and engineer's approval. The contractor should submit sample for approval from the Engineer before starting. The material used must have a valid quality certification from the Palestinian Institue for Standards and Measurements and pass all tests of paintings as conducted in authorized lab |  |  |  |  |
| 6.01 | Supply and paint bondrol primer coat and three coats of emulsion paint (Supecryl) for internal walls including all the required materials as shown on the drawings, specifications and Engineer's instructions. | m2 | 800 |  |  |
| 6.02 | Supply and paint oil paint for internal existing walls( three coats ) the item include removing the cracks of old paint , using putty in areas where cracks removed untill having plain surface, smoothing the walls, cleaning the surface very well in the areas where the supervisor engineer indicates to prepare it to new painting ,the item including a pendrol layer before oil paint & all the required materials according to specifications and Engineer's instructions.. | m2 | 210 |  |  |
|  | Total Bill No.6 (Carried to summary) |  |  |  |  |
| Note: All relevant specifications requirements, drawings, and details are to be taken into account. |  |  |  |  |  |

| Bill No.7 (Tiling And Marble Work) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item No. | Description | Unit | Qty | Rate NIS | Amount NIS |
|  | The items (tiling and marble works) include supplying and testing of all required material and providing all required workmanship. All tilling works must be filled and mechanically polished according to the specifications, drawings and engineer's instructions. Samples of used materials should be submitted to the engineer for approval before starting. Ceramic tiles type & color & marble type & color according to Engineer instructions. |  |  |  |  |
| 7.01 | Supply and install colored glazed wall ceramic tiles (European style) laid on mortar backing morter ratio 3:1 for walls of halls & rooms& corridors that will be tiled as shown in drawings and according to the supervisor instructions . The price include stainless steel angles at corners where needed ( the angle is 3mm thick. 5*5cm and the same height as the ceramic wall and to be formed at angle 135 or 90 as needed ), and also includes removing existing plastering in these locations that will be replaced with ceramic tiles to reach existing block and making rough concrete layer to lay the tiles on it. | M2 | 450 |  |  |
| 7.02 | Supply and install white glazed wall tiles (ceramic) size 20cm x20cm x 5mm thick laid on mortar backing. The price include decoration works, aluminum angles at corners. | M2 | 150 |  |  |
| 7.03 | Supply and install white non-sliding ceramic floor tiles size 20cm x 20cm x6mm thick. The price includes decoration works and using plastic (Voka) cross 3mm thick. | M2 | 25 |  |  |
| 7.04 | Supply and lay colored glazed non sliding porcelain ( European Type)( full body) floor tiles size 40x40x0.8cm laid on 2.5cm mortar bed and 5cm thick sand bed with skirting size 40x10x1cm. | M2 | 50 |  |  |
| 7.05 | Supply and lay floor mozaic tiles (with marble chips) size 30*30*3 cm laid on 2.5cm mortar bed and 5cm thick sand bed with skirting size 30x10x3cm. | m2 | 420 |  |  |
| 7.06 | Supply and erect local marble (Kahlili type YATTA First Class with marbel in some parts) type A for cupboards 60cm wide and 90 cm high including vertical dividers 3cm thick, internal horizontal shelves 2 cm thick, floors 2 cm thick and granite 2cm thick (Orez) for the top surface with round edges, Skirting 10cm high (Orez), sand fill, aluminum leaves and making the needed opening for basins as showing in drawings for the Kitchens and Laboratories. | L.M | 2.4 |  |  |
|  | Total Bill No.7 (Carried to summary) |  |  |  |  |
| Note: All relevant specifications requirements, drawings, and details are to be taken into account. |  |  |  |  |  |

| Bill No. 8 (Proofing Works) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item No. | Description | Unit | Qty | Rate NIS | Amount NIS |
|  | PVC Covering |  |  |  |  |
| 8.01 | Supply and install pvc flooring (roll) -type Traflex or equivalent thickness of 2mm , according to the specifications &the following conditions: 1 -Supply and lay floor trrazzo tiles size 25x25x2.5cm thick laid on 2.5cm mortar bed and 5cm thick sand bed with skirting of same shape size 25x7x1cm, 2 - Using cealant to close any tile joints & to settle the tiles . 3 -Smoothen the cealant between tiles and clean the floor out of dust using dust suction device to make sure having very smooth & clean floor. 4 - Laying a fast glue -type (K1), taking into account the absence of bubbles of air. 5 - Installation of pvc roll carefully taking into account the absence of bubbles of air, and make sure keeping overlapping areas of not less than 2mm for welding process between the sheets 6 - Installation of Aluminum strips at the end of pvc at the door opening ( convex aluminum ) 7 - Installation of skirting of the same type and color of pvc on the walls and taking in consideration making angle fillets as specifications and instructions of engineer . 8 - Using transparent (Postic) at the small and narrow locations . 9 - Clean and polished the floor and finish all works as instructed by the supervising engineer. 10 -The measurements are for the horizontal area | m2 | 55 |  |  |
|  | Supply and lay sheets of lead 2mm thick for covering the wall and floors of x-ray room as per drawings. | m2 | 70 |  |  |
| 8.02 | Supply and install antibacterial and fungi false ceiling manufactured by Armstrong or equivalent of 60*60cm with exposed suspension system including galvanized steel hangar wire, hold down clip, wall molding, main and cross bar, as specified shown drawing and engineer's approval. The suspension parts will be selected by the Engineer. The works shall include the Gypsum borders to close the sides. | m2 | 35 |  |  |
| 8.03 | Supply and install false ceiling manufactured by Armstrong or equivalent of 60*60cm with exposed suspension system including galvanized steel hangar wire, hold down clip, wall molding, main and cross bar, as specified shown drawing and engineer's approval. The suspension parts will be selected by the Engineer. The works shall include the Gypsum borders to close the sides. | m2 | 375 |  |  |
|  | Total Bill No.8 (Carried to summary) |  |  |  |  |
| Note: All relevant specifications requirements, drawings, and details are to be taken into account. |  |  |  |  |  |

Bill No. 9  (Mechanical Works )

| FIRST ( HVAC WORKS) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Ref. | DESCRIPTION |  | Qty | Unit | Unit Price NIS | Amount NIS |
|  | Note :1 |  |  |  |  |  |
|  | All following items shall be executed according to drawings, specifications and as directed by the Engineer. Prices shall include all required works, fittings , connections , accessories and testing. |  |  |  |  |  |
|  | Note :2 |  |  |  |  |  |
|  | Contractor shall submit shop drawings for all Mechanical installations to be approved by the Engineer before executing the work. As-Built drawings shall be submitted after completing the work |  |  |  |  |  |
| 1.01 | Dismantle and remove all the existing Air conditioning System parts like units, ducts, hangers, etc.. And submit completely to the MOH Representative in a neat and organized manner |  | 1 | LS |  |  |
| 1.02 | clean, maintain, install, test and commission the removed wall mounted split AC unit in the new location with all the related works according to specified location by the engineer, drawings, and relative specification. |  | 6 | No. |  |  |
| 1.0 | Ducted Split Unit: |  |  |  |  |  |
| 1.1 | Supply, install, test and commission Ducted Central Split Heat Pump Unit (DSU- 0X) SKM, Gonka, York, or equivalent air conditioning for the ground floor , filled with environment friendly refrigerant such as (R410, R407c,..) composed of out door unit. COP should not be less than 3.5, with mixing box, Well supported on galvanized steel base on the roof, indoor unit roof mounted as indicated on drawings to be tights installed completed with all necessary supports, hangers, drain pipes from indoor unit to the nearest floor drain ( PVC Ø 1"), cupper pipes, sleeves, thermostat, with fresh air, humidity controlling, insulation, aluminum foil and all related work and all required electrical cables according to drawings and engineers approval. CAPACITY : (12 TR), (3700cfm), and (570 cfm Fresh Air) (DSU-02) |  | 1 | No. |  |  |
| 1.2 | Dittu, but for the Ground floor with CAPACITY: (3TR), (658 cfm) &(150 cfm Fresh Air) (DSU-1) |  | 1 | No. |  |  |
| 1.3 | Dittu, but for the Ground floor with CAPACITY: (2.5 TR), (840 cfm) and (120 cfm Fresh Air) (DSU-04) |  | 1 | No. |  |  |
| 2.0 | Extract Fan |  |  |  |  |  |
| 2.1 | Supply , install, test and commission Wall Mounted Extract Fan with backdraft shutters,to be tights installed completed with all necessary supports, sleeves, dampers, and all required electrical cables , and should be working with (DSU) According to drawings and engineers approval. CAPACITY : (315 cfm). EXF.1 working with (DSU- 02,03). |  | 2 | No. |  |  |
| 2.2 | Dittu, but CAPACITY: (155 cfm), Static Pressure 20 Pascal. EXF.2 working with (DSU-01) |  | 1 | No. |  |  |
| 2.3 | Dittu, but CAPACITY:(135 cfm), Static Pressure 20 Pascal. EXF.2 working with (DSU-05) |  | 1 | No. |  |  |
| 3.0 | Duct Works : |  |  |  |  |  |
| 3.1 | Supply, install, test, and commision insulated galvanized sheet ducts (min. thick : 0.7 mm), with a proper gages as specified by SMACNA for Supply, Return, including 2" rock wool insulation 24kg/m3 all accessories, galvanized ' L' angle hangers (2x40x40), with 10mm rods, bolts, flexible connector, with duct liner for at least 3m length from unit, and with aluminum foil, to be connected to the DSU units and all the requirements according to SMACNA and other relevant international standards, drawings, and Engineers instructions. |  | 150 | M2 |  |  |
| 3.2 | Dittu, but without insulation for Fresh and Exhaust Air Ducts. |  | 40 | M2 |  |  |
| 4.0 | Air Distributing Equipment |  |  |  |  |  |
| 4.1 | Supply, Install, test, and commission anodized finish 4 ways square aluminum Ceiling Diffusers for supply air. Price should include plenum boxes. Noise Rating Should not exceed 40db all according to SMACNA and other relevant international standards, drawings, and Engineers instructions, Neck: 300x300, face:450x450 (75-105 l/s) |  | 35 | No. |  |  |
| 4.2 | Supply, Install, test, and commission anodized finish 4 ways square aluminum Ceiling Return air grill. Noise Rating Should not exceed 40db all according to SMACNA and other relevant international standards, drawings, and Engineers instructions, face:600x600 (70-110 l/s) |  | 28 | No. |  |  |
| 4.3 | Supply, install, test, and commission anodized finish aluminum grill for return air, 0 deg. horizontal blade deflection with 3/4" blade spacing all According to SMACNA and other relevant international standards, drawings, and engineers instructions Neck: 350x200 mm, face: 500x300, for the 234 l/s, |  | 1 | No. |  |  |
| 4.4 | Dittu, but Size: 400x250 mm, for the 339l/s |  | 1 | No. |  |  |
| 4.5 | Supply, install, test, and commission anodized finish aluminum grill for Fresh air, 45 deg blade deflection with 3/4" blade spacing all According to SMACNA and other relevant international standards, drawings, and engineers instructions Neck: 350x200 mm, face: 500x300, for the 340 l/s, |  | 1 | No. |  |  |
| 4.6 | Dittu, but Neck: 250x100 mm, Face: 350x150 mm |  | 2 | No. |  |  |
| TOTAL HVAC WORKS |  |  |  |  |  |  |
| SECOND (FIRE FIGHTING WORKS) |  |  |  |  |  |  |
| 5.0 | Fire Fighting Network |  |  |  |  |  |
| 5.1 | Supply, install, test, and commission galvanized black steel pipes for fire fighting water pipe line coated with red corrosion resistant paint. Price should include all the hangers, bolts, fixtures, elbows, supports, excavation, backfilling, connections all according to the relevant international standards, drawings& engineers approval Size: Dia 2" | 20 |  | LM |  |  |
| 5.2 | Ditto, but Size: Dia: 1 1/2" | 17 |  | LM |  |  |
| 5.3 | Ditto, but Size: Dia: 1" | 17 |  | LM |  |  |
| 5.4 | Ditto, but Size: Dia: 3/4" | 6 |  | LM |  |  |
| 5.5 | Supply, Install, connect and test a European made fire fighting retractable spring loaded Hose Reel cabinets (80x80x25)cm, made of at least 1.5mm Galvanized Steel coated with anti-corrosion paint, the cabinet should include a 3/4" ball valve, landing valve, and nozzle, all according to specifications, drawings and engineers approval | 2 |  | No. |  |  |
| 5.6 | Supply and Install CO2 fire extinguisher according to specification, drawings,& Engineers Approval Size: 6 kg | 2 |  | No. |  |  |
| TOTAL FIRE FIGHTING WORKS |  |  |  |  |  |  |

| THIRD (SUPPLY WATER WORKS) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 6.0 | SUPPLY WATER WORKS |  |  |  |  |
| 6.1 | Supply, Install, test, and commission 16 bar Ø2" G. St. pipe for cold water supply lines. The price should include all the line valves, elbows, drilling, excavation, backfilling, connections to the existing pipes, supports,& all the requirements. The pipe and its installation should be according to the relevant international supply water piping standards and according to Drawings, Specifications,& Engineers instructions | 25 | LM |  |  |
| 6.2 | Dittu, but Ø1 1/2" | 35 | LM |  |  |
| 6.3 | Dittu, but Ø1" | 15 | LM |  |  |
| 6.4 | Dittu, but Ø3/4" | 15 | LM |  |  |
| 6.5 | Supply, Install, test, and commission 16 bar Ø1.5 " insulated G.St. pipe for Hot water supply lines. The price should include all the line 1" polyethylene insulation, valves, elbows, drilling, excavation, backfilling, connections to the existing pipes, supports, and all the requirements. The pipe and its installation should be according to the relevant international supply water piping standards and according to Drawings, Specifications & Engineers instructions | 25 | LM |  |  |
| 6.6 | Dittu, but Ø 1" | 35 | LM |  |  |
| 6.7 | Dittu, but Ø 3/4" | 15 | LM |  |  |
| 6.8 | Supply, Install, Test and commission 60X40X8 cm Water G. St. Distribution box painted with epoxy coating with Aluminum Door with 2 internal copper manifold with outlets matching the drawings quantities plus 2 outlets spare with valves at the inlet and each outlet line. The price must include all the accessories according to relevant international standards, specifications, drawings, and Engineers instructions. | 3 | No. |  |  |
| 6.9 | Supply, install, test& commission under ground Ø16 mm Golany lines from the distribution box to the sanitary fixtures. The price must include the pvc sleeve, elbows, supports, accessories, etc. & all needed for complete installation according to relevant international standards and according to drawings, specifications& Engineers instruction | 240 | LM |  |  |
| TOTAL Supply Water Works |  |  |  |  |  |

| 7.0 | Sanitary Works |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 7.1 | Supply, install, test and commission Vitreous China wash basin (58x44cm) Vitra or approved equivalent, completed with chrome plated Jack type mixer, bottle trap, soap tray, chrome plated angle valves, flexible tubes, mirror and all accessories, supports and hangers all according to specifications, drawings, and Engineers instructions | 12.0 | No. |  |  |
| 7.2 | Supply and install Stainless Steel Sink for hand washing in the rooms - Foster type (S4000 Sottop -Cabinet 80)or approved equivalent, out side dimensions (58cm x 45cmx 22cm), with vertical drain easy to clean , with chrome plated sink mixer (opened by long arm type Hamat or approved equivalent) , Including all necessary fittings and connections, angle valves, chrome plated chain and rubber plug connections, all necessary supports, pipes, vent pipes ,cap for ventilation pipes. The item includes supply and install Soap dispenser & Paper towel dispenser from approved type with all fittings . The item includes supply and erect local marble first class type (Yatta ) , 60cm wide and 80 cm high including vertical sides 3cm thick, internal horizontal shelf 2 cm thick for holding the sink, a floor 2 cm thick and granite top counter (rozabitta type) 3cm thick. with round edges with dimensions (60*100 cm), Skirting 10cm high (rozabitta type), sand fill, aluminum and fiber 2 leaves ,filling openings using (bostek) and making the needed opening for the sink. All according to drawings and supervisor engineer instructions. | 4 | No. |  |  |
| 7.3 | Supply, install, test and commission Stainless Steel Sink table for the buffets and Gypsum room with one sink and side stainless steel table with dimensions 60X150X22 cm to be fixed with jack type long chrome plated mixer with all the chrome plated pipes, fixtures, rubber, chain, etc.. complete to drain according to drawings, specifications and engineers instructions | 2 | No. |  |  |
| 7.4 | Supply and install Vitreous China, European type, W.C. Vitra or approved equivalent, completed with 4” pipes, 2.5 Gallon flush reservoir, roll holder, chrome plated angle valves and flexible connections, supports, hand spray with flexible chrome connections, holder, and fittings, heavy duty cover, rubber connector on WC outlet to the drain pipe all according to relevant international standards, specifications, drawings and Engineers instructions | 6.0 | No. |  |  |
| TOTAL Sanitary Works |  |  |  |  |  |

| Forth (DRAINAGE WORKS) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 8.0 | Drainage Works |  |  |  |  |
| 8.1 | Supply, Install, test, and commission 2" UPVC 10 bar Pipes for drainage system. The price must include any modifications, boring, demolishing, cutting, and connections. The price must also include all the required accessories, connections, elbows, tees, rubber, etc.. to connect to the Sanitary fixtures and all the rquirement for the complete installation according to the relevant international drainage standards and according to Drawings, Specifications, and Engineers instructions | 50 | LM |  |  |
| 8.2 | Dittu, but 4" | 120 | LM |  |  |
| 8.3 | Supply, Install, test, and commission 4" UPVC Floor Drain and collector with St. Steel strainer and cover. the floor drain and Its installation should be according to the relevant international standards and according to Drawings, Specifications, and Engineers instructions. | 15 | NO. |  |  |
| 8.4 | Supply, Install, test, and commision 60 cm dia manhole with 50cm dia 8 ton cast iron cover. Manhole must be internally and externally tar coated for isolation and sealing. The price should include all excavation, fittings, leveling, connections, sealing, backfilling, etc.. All according to the relevant international standards, drawings, specifications, and Engineers instructions | 1 | NO. |  |  |
| 8.5 | Supply, install, test, and commision UPVC Floor Clean Out with PVC cover. The Clean Out and its installation should be according the relevant international standards, specifications, drawings, and Engineers instructions | 2 | NO. |  |  |
| 8.6 | Supply, Install, test, and commission 4" UPVC 6 bar Pipes for rain drainage system. The price must include any modifications, boring, demolishing, cutting, and connections The price must also include all the required accessories, connections, elbows, tees, rubber, etc.. to connect to the Sanitary fixtures and all the rquirement for the complete installation according to the relevant international drainage standards and according to Drawings, Specifications, and Engineers instructions | 16 | LM |  |  |
| TOTAL Drainage Works |  |  |  |  |  |

| FIFTH (MEDICAL GASES WORKS) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 9 | Dismantle and remove all the existing Medical gases System parts like copper Pipes, Panels, BHUs, hangers, etc.. And submit completely to the MOH Representative in a neat and organized manner | 1 | ls |  |  |
| 9.1 | Supply, Install, and test Genetic, George Samaras, Silbermann, or equivalent valve control box for 3-gases Containing 5 full-port NIBCO shut off valves which controls the supply of gases or vacuum through the pipelines and a line pressure gauge for each gas, recessed type, the front is made of transparent polycarbonate flexible unbreakable cover to ease access in emergency situation | 1 | NO. |  |  |
| 9.2 | Supply, Install, and test Genetic, George Samaras, Silbermann, or equivalent line pressure alarm for 5 gases JAVA 2000 local audio-visual line pressure alarm to indicate pressure and vacuum failures by means of green LED, red LED, audio buzzer and pressure or vacuum gauge for each gas, operated by means of one central PC card (microprocessor card) and pressure/vacuum switches for each gas, recessed type. | 3 | NO. |  |  |
| 9.3 | Supply, Install, and test Genetic, Cleantica, Silbermann or equivalent Bed head unit for two beds Encompassing extruded aluminum duct system, with four cavities, three of which are directly accessed using snap-on covers. Supplying electrical and lighting service, Three piece ball-type Valves, as well as medical gas service, including the following preparations for each patient bed: One oxygen outlet One Medical air outlet One vacuum outlet 2 electrical sockets, Main line 2 electrical sockets, UPS lineone potential grounding socket indirect light (simplex fluorescent 58 W)direct light (2 PL BIAX lamps) cut-off switch for direct / indirect lights one telephone socket preparation for nurse call socket | 1 | NO. |  |  |
| 9.4 | Ditto but for four beds | 1 | NO. |  |  |
| 9.5 | Ditto but for Seven beds | 1 | NO. |  |  |
| 9.6 | Supply, Install, and test type (L) Degreased medical gases compatible seam-less copper pipes. The pipes must be cleaned and treated for medical gas usage including capping the ends of each pipe to ensure that no foreign bodies or dust or vapors affect the pipes The copper pipes must meet with the international standard of ASTM B-819 and to be cleaned for medical usage (degreased) in accordance with CE 0473: Diameter ½” Inch | 50 | LM |  |  |
| 9.7 | Diameter 5/8” Inch. | 60 | LM |  |  |
| 9.8 | Diameter 1” Inch. | 55 | LM |  |  |
| 9.9 | Diameter 1 1/2” Inch. | 55 | LM |  |  |
| TOTAL MEDICAL GASES WORKS |  |  |  |  |  |
| TOTAL MECHANICAL WORKS |  |  |  |  |  |

| Electrical Works |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item No. | Description | Unit | Qty | Unit Rate NIS | Amount NIS |
|  | supply, install, test, commission & operate the electrical works as per drawings, specifications, and engineer's instructions. The price of the following items includes all necessary junction boxes , Cu. wires , labels (all circuit, switches, sockets, cables) conduits, clamps, bolts, connectors and connecting all cables to switch boards. |  |  |  |  |
|  | Contractor shall submit shop drawings for all Electrical installations to be approved by the Engineer before executing the work. As-made drawings shall be submitted after completing the work. |  |  |  |  |
|  | All installation shall be in accordance with : ♦ The drawings , specifications and instructions and demands of the engineer. ♦ The electricity law and electrical code requirements of the BRITISH standards. ♦ The contractor should refer to the drawings , specifications and other Contract Documents . ♦ The prices will be deemed to include for the full cost as described in all Documents. ♦ All roof electrical items should be waterproofed and sun proofed |  |  |  |  |
|  | Electrical works |  |  |  |  |
| Section 1 | Lighting Fittings, Ceilling fans, and Extractor fans |  |  |  |  |
| Section 2 | Switches & Sockets: |  |  |  |  |
| Section 3 | Telephone and Computer |  |  |  |  |
| Section 4 | Fire Alarm System |  |  |  |  |
| Section 5 | Electrical Distribution Boards & Circuit Breakers |  |  |  |  |
| Section 6 | Cables and Cable tray |  |  |  |  |
| Electrical works |  |  |  |  |  |
|  | Section 1 |  |  |  |  |
|  | Lighting Fittings, Ceilling fans, and Extractor fans |  |  |  |  |
| 1 | Ceilling mounted fluorescent lighting fixture 2x36w complete with lighting tubes 36, chock coil, condensers, starters rigid PVC conduits, J.boxes, fixing screws (Galv.) and wiring. (Type is GA'ASH No. 50540 or equivalent) | No. | 7 |  |  |
| 2 | Ditto, as (1) but water and dust proof IP65 2x36W. (Type is GA'ASH No. 52940 or equivalent) | No. | 4 |  |  |
| 3 | Ditto, as (1) but 1x36w (Type is GA'ASH No. 50530 or equivalent) | No. | 10 |  |  |
| 4 | Ditto, as (1) but 4x18w. (59.5X59.5 cm) with opal diffuser for false ceiling mounting. (Type is GA'ASH No. 54450 or equivalent) | No. | 9 |  |  |
| 5 | Ditto, as (1) but 4x18w. (59.5X59.5 cm) with mirror reflector for false ceiling mounting. (Type is GA'ASH No. 53820 or equivalent) | No. | 95 |  |  |
| 6 | Ditto, as (1) but circular luminaire with 26W PL lamp (Type is GA'ASH No. 552100 or equivalent) | No. | 14 |  |  |
| 7 | Dark Room Red Light Fixture with 25W Bulb, on/off switch & filter ( type is Agfa or Equivalent) | No. | 1 |  |  |
| 8 | Emergency lighting fixture 8w, 1.5hrs. duration with self adhesive PVC "exit" legend complete with all necessary accessories. (type is GA'ASH No.589220 or equivalent ) | No. | 4 |  |  |
| 9 | Ceiling fan complete with wiring and regulator switch. (Type is El Araby or equivalent) | No. | 7 |  |  |
| 10 | 6" Extractor fan 250 cfm with movable louvers, and any required thing (such as 6" pipes") to complete the work (Type is VENTA or equivalent). | No. | 3 |  |  |
|  | Section2 |  |  |  |  |
|  | Switches & Sockets: |  |  |  |  |
| 11 | Single pole one way switch, 220v, 10A, complete with PVC conduits, J. boxes, wiring, cover and all necessary accessories. (Type is bticino original or equivalent). | No. | 16 |  |  |
| 12 | Ditto, as (11) but waterproof. | No. | 7 |  |  |
| 13 | Ditto, as (11) but one way, two pole switch | No. | 4 |  |  |
| 14 | Ditto, as (13) but waterproof. | No. | 1 |  |  |
| 15 | Ditto, as (11) but two way, one pole switch | No. | 6 |  |  |
| 16 | Ditto, as (11) but two way, two pole switch | No. | 4 |  |  |
| 17 | Ditto, as (11) but one way, three pole switch | No. | 5 |  |  |
| 18 | Ditto, as (11) but one way, four pole switch | No. | 1 |  |  |
| 19 | Single socket outlet 16A, 220v, 2p+E for flush or surface mounting, complete with PVC conduits, J. boxes, wiring, and all necessary accessories. (Type is bticino original or equivalent). | No. | 31 |  |  |
| 20 | Double socket outlet 16A, 220v, 2p+E for flush or surface mounting, complete with PVC conduits, J. boxes, wiring, and all necessary accessories. (Type is bticino original or equivalent). | No. | 42 |  |  |
| 21 | Ditto as item (19) but water proof type.. | No. | 2 |  |  |
| 22 | Single AC socket outlet 16A, 220v, 2p+E for flush or surface mounting, complete with PVC conduits, J. boxes, wiring, and all necessary accessories. (Type is bticino original or equivalent). | No. | 1 |  |  |
| 23 | Isolating switch (3X63A) for AC Ducted split units IP65 inside water proof enclosure (Type is moeller or equivalent P3-63/I4/SVB-SW/N) c/w xlpe Cu. Cabel 5x6mm2 from the switch location to related SDB ( switch to be fixed beside outdoor unit). | No. | 22 |  |  |
| 24 | Isolating switch (3X32A) for AC Ducted split units IP65 inside water proof enclosure (Type is Moeller or equivalent P1-25/I2/SVB-SW/N) c/w xlpe Cu. Cabel 5x4mm2 from the switch location to related SDB ( switch to be fixed beside the indoor unit. | No. | 3 |  |  |
| 25 | Isolating switch (2X32A) for AC split units (Type is moeller or equivalent I2/SVB-SW) c/w xlpe Cu. Cabel 3x4mm2 from the switch location to related SDB | No. | 6 |  |  |
|  | Section3 |  |  |  |  |
|  | Telephone and Computer. |  |  |  |  |
| 26 | Sub-telephone box 40x60 cm complete with all connection strips (5x10 pair), termination and all necessary accessories. | L.S. | 1 |  |  |
| 27 | Wall mounted telephone socket outlet 6 pin complete with PVC conduits, J.boxes, 2 pairs shielded cable (Teldor), and all necessary accessories (Type is bticino matix original or equivalent). | No. | 20 |  |  |
| 28 | 50 pair telephone shielded cable to connect the new sub-telephone box "T-Box-1" with the main telephone box located in the first floor of building and all necessary accessories. | L.M. | 40 |  |  |
| 29 | Internal complete computer sockets (single) with RJ45 cat 5e (Type is bticino original or equivalent). female connectors, cover, connect it to the patch panel in IDFs (racks) with FTP cables cat 5e teldor as shown in the network drawings, all sockets must be tested and labeled(cables, sockets). | No. | 24 |  |  |
| 30 | Wistern Wire PATCH PANEL- cat 5e 24 PORTS with RJ45 Female Connector Rack Mount with standard Cable Cat 5e to connect Patch Panel with Switch including necessary RJ's, ,approximate 30cm length. | No. | 1 |  |  |
| 31 | Rack 10 U – with removal sides, Fans. | No. | 1 |  |  |
| 32 | Cisco Catalyst switch 2960-24. Switch Type: Rackmount. Ports:10/100 + 2 1000BT LAN Base Image. | No. | 1 |  |  |
|  | Section4 |  |  |  |  |
|  | Fire Alarm System |  |  |  |  |
|  | fire alarm system including fire resist PVC pipes, pull boxes special wires and all necessary wires and accessories. According to specifications and demands of the supervising engineer .(Type is TELEFIRE or equivalent): |  |  |  |  |
| 33 | Fire alarm control panel 8 zones complete with brand name original batteries, the item include 2pair cable for the fire alarm network and all necessary accessories needed to complete the job. (Type is TELEFIRE or equivalent) | No. | 1 |  |  |
| 34 | Ionization smoke detector, the detectors shall be twin-chamber with latching electronic circuitry, two wire connection.(Type is TELEFIRE or equivalent) | No. | 38 |  |  |
| 35 | ditto, as (31) but heat detector. | No. | 1 |  |  |
| 36 | Break glass call point for interior use with key operated test facility, wiring, with plastic coated glass.(Type is TELEFIRE or equivalent) | No. | 4 |  |  |
| 37 | 95 db electronic horn ultra sound for indoor use.(Type is TELEFIRE or equivalent) | No. | 3 |  |  |
| 38 | 95 db electronic horn ultra sound with flasher for outdoor use.(Type is TELEFIRE or equivalent) | No. | 1 |  |  |
|  | Section5 |  |  |  |  |
|  | Electrical Distribution Boards & Circuit Breakers |  |  |  |  |
|  | Supply, install, test and commission electrical distribution boards including all circuit breakers as specified and as shown on related drawings, factory assembled wired and tested in accordance with international standards, including 2mm Galv.steel frame with anti static paint including busbars neutral bus bar, earthing terminal and all necessary civil works, cable trenches and handing over clean, tested and in operating conditions. (Type is MOELLER or equivalent). According to drawings , specifications and demands of the engineer, as follow: |  |  |  |  |
| 39 | Sub distribution board "SDB-1" as shown on drawings (E-06), | set | 1 |  |  |
| 40 | Sub distribution board "SDB-2" as shown on drawings (E-07), | set | 1 |  |  |
| 41 | Sub distribution board "SDB-Xray" as shown on drawings (E-07) | set | 1 |  |  |
| 42 | Sub distribution board "SDB-UPS" as shown on drawings (E-07) | set | 1 |  |  |
| 43 | Supply, install, connect and test true on-line, double-conversion, transformer UPS 3KVA (1in/1out) according to specifications and engineers instructions, complete with all necessary accessories, (Type is Gamatronic or equivalent). According to the attached ups specifications. | set | 1 |  |  |
| 44 | Supply, install, connect and test true on-line, double-conversion, UPS 650 VA (1in/1out) complete with all necessary accessories, to be installed inside the computer rack (Type is Smart APC or equivalent). | set | 1 |  |  |
| 45 | Molded case circuit breaker with (over load protection) MCCB 3x125 A. (Type is MOELLER NZMN1-A125 or equivalent). To be installed in the main distribution board to feed the new Essential loads cable. | No. | 1 |  |  |
| 46 | Molded case circuit breaker with (over load protection) MCCB 3x80 A. (Type is MOELLER NZMN1-A80 or equivalent). To be installed in the main distribution board to feed the new cables. | No. | 2 |  |  |
| 47 | Miniature circuit breaker with (over load protection) MCB 3x40 A. (Type is MOELLER or equivalent). To be installed in the main distribution board to feed the new cable. | No. | 1 |  |  |
|  | Section6 |  |  |  |  |
|  | Cables and Cable tray |  |  |  |  |
|  | supplying, connecting, and termination of XLPE cu cables and Cable tray with all required electrical and civil works to connect cable terminals from source to destination. According to drawings, specifications and demands of the supervising engineer. as follow: |  |  |  |  |
| 48 | (3x50+25)+25 mm2 XLPE Cu cable | L.M | 50 |  |  |
| 49 | (3x25+16)+16 mm2 XLPE Cu cable | L.M | 100 |  |  |
| 50 | 5x10 mm2 XLPE Cu cable | L.M | 40 |  |  |
| 51 | Dismantling and reinstalling the existing cable tray as shown on drawing (E-08) and according to engineer's instructions, the item includes all nessesary supports and accessories to complete the work. | L.S | 1 |  |  |
| 52 | Galvanized steel cable tray 30X7 cm cable trays ( at least 1 mm thickness) for power cables including supports and all accessories. | L.M | 35 |  |  |
|  | Intercom system according to engineers instructions, complete with 1 No. handset, 2 door stations (loud speakers with 2 push buttons) , electric door lock type is ISO, power supply & servic module with all required cables , junction boxes conduits and all necessary accessories (Type is Farfisa or equivalent). | L.S | 1 |  |  |
| 53 | Dismantling all of the old Electrical Network according to engineer's instructions and handing over all the material to engineering and maintenance Department. | L.S | 1 |  |  |
| Discount |  |  |  |  |  |
| Total Price in NIS VAT Excluded |  |  |  |  |  |

# Section IV

Technical Specifications

contractorContractorcontractorcontractorcontractorcontractorcontractor

CONTENTS

I. GENERAL	58

1.DEMOLITION WORKS	59

1.1.General Demolition:	………….59

1.2 removal, Reinstatement And/Or Relocation Of Obstructions, Pipelines, Pavement & Utilities 61

1.3Removal and Relocation of Pipes, Conduits etc.	62

1.4Cleaning of Sewerage Structures to be Abandoned or Destined to Other Uses:	62

1.5Backfilling of Abandoned Structures	63

1.6Abandonment of Existing Pipelines	63

1.7Demolition of existing Road Pavement	64

1.8Removal of Side Walk, Concrete Paving:	64

1.9Reinstatement of Surfaces	64

1.10Removal of Road Furniture	65

1.11Removal of Fence	65

2. EXCAVATION  WORKS	65

2.1.Datum and Nature of Excavation	65

2.2. Site Preparation	66

2.3. Existing Utilities	66

2.4. Removal of Existing Structures and Other Obstructions	66

2.5. Cleaning and Grubbing	66

2.6.Setting Out	67

2.7.Surface Leveling	67

2.8.Size and Depth of Excavation	67

2.9.Shoring Excavation	68

2.10.Types of Excavations	68

2.11.Lack of Required Bearing Capacity	68

2.12.Preparation and Inspection of Excavations	68

2.13.Filling	69

2.14Cutting Pavement and Surface Materials	70

2.15.Excavation & Preparation of Tender Formation	70

2.16. Protection of Existing Services	71

2.17. Backfilling of Trenches	72

2.18.Disposal of Surplus Material	72

3. CONCRETE WORKS	73

3.1.Cement	73

3.2.Aggregates	73

3.3.Handling Aggregates	76

3.4.Water	76

3.5.Quality of Concrete	76

3.6.Adjustment of Mix Proportions	78

3.7.Batching and mixing of Concrete	78

3.8.Prescribed mixes for ordinary structural concrete	79

3.9. Work in Cold or Hot Weather	80

3.10.Reinforcement	81

3.11Minimum Cover	82

3.12.Formwork for Concrete	83

3.13.Joints	84

3.14.Placing	85

3.15.Admixtures	86

3.16.Curing	86

3.17.Fair-Faced Finish	87

3.18.Other Types of Concrete	87

3.19.Testing	87

3.20.Protection.	88

4. MASONRY WORKS	90

4.1.General	90

4.2.Mortars	91

4.3.Construction	92

4.4Labors	93

4.5.Damp-proof course	93

5.METAL AND ALUMINIUM WORKS	94

5.1 Generally	94

5.2.Aluminum Windows	94

5.3.  Aluminum Curtain Walling	99

5.4. Sundries	100

5.5. Custom Steel Door and Frame	100

6. IRONMONGERY	107

6.1.Generally	107

6.2 Finish	107

6.3 Fitting and testing	107

7. STRUCTURAL STEEL WORKS	108

7. 1 .  Structural Steelworks	108

8. INSULATIONS	108

8.1 Bitumen Paint	108

8.2 Installation Of General Building Insulation	108

8.3Insulating Materials	109

8.4Vapor Retarders	111

8.5Auxiliary Insulating Materials	112

8.6Insulation Fasteners	112

8.7Roofing Insulation	113

9. PLASTER WORK AND OTHER WALL AND CEILING FINISHES	118

9.1.MATERIALS	118

9.2.Mixing	119

9.3.Workmanship	119

9.4.Preparation	120

9.5.Curing	120

9.6.Application	120

9.7.Wall Tiling	121

9.8.Glass Mosaic:	121

9.9.Carpentry works	123

10. PAINTING AND DECORATING	126

10.1.Generally	126

10.2.Materials	127

10.3.Internal Plaster, Fair faced Concrete and Block work	129

10.4.Ceiling Boards etc.	129

10.5.Steelworks including Windows, Louvers, etc. Internally and externally.	129

10.6.Exposed Service Pipes	130

10.7. Woodwork required to be painted	130

10.8. Woodwork required to be stained and varnished.	131

10.9 FINISHING PROGRESS	131

11.PAVIOR (INCLUDING MARBLE AND TERRAZZO WORKER)	132

11.1. Materials	132

11.2 Mixing	133

11.3 Proportions	133

11.4 Granolithic Paving	133

11.5 Cement and sand paving	134

11.6 Cement and sand tiles	134

11.7 Terrazzo Tiles	135

11.8 Marble Paving	136

11.9 Marble linings	136

11.10 Generally	137

11.11 Tiles Testing	137

11.12 Tiles and Cladding	137

11.10 Porcelain Wall tiles	138

12.GLAZING	139

12.1 Materials	139

12.2 Plate glass	139

12.3 Obscured glass	140

12.4 wired Glass	140

12.5 Heat-absorbing glass	140

12.6 Armourpslate glass	141

12.7 Mirror glass	141

12.8 Putty	141

12.9 Glazing beads	141

12.10 Glazing to wood without beads	141

12.11 Glazing to wood-with beads	142

12.12 Glazing to metal-without beads	142

12.13 Galzing to metal – with beads	142

12.14 Glazing without putty	142

12.15 Mirrors	142

12.16 Cleaning etc.	142

13.CARPENTRY AND JOINERY	142

13.1 Timber	142

13.2 Moisture content of timber	143

13.3 Plywood	143

13.4 Face veneers	143

13.5 Asbestos insulating board	144

13.6 Fixings and jointing	144

13.7 Doors	144

13.8 Windows and Sashes	144

13.9 Hatches and shutters	144

13.10 Fly screens	144

13.11 Frames	144

13.12Fittings	145

13.13 Shelving	145

13.14 Scribing	145

13.15 Finish	145

13.16 Protect joinery from damage	145

14.ROOF FINISHES:-	145

14.1SPECIFICATIONS	146

15. ROADS WORK	150

15.1 Earthwork And Road Excavation	150

15.2sub-Base And Base Courses	157

15.3 Concrete Block Paving	166

15.4 Bituminous Construction	171

16.EQUIVALENT STANDARDS	199

# I. GENERAL

This General Specification is intended to provide overall guidance in the Rehabilitation of Emergency Department at Shohadaa Al Aqsa Hospital and shall apply to all Building and Engineering Works.

The General Specification shall always apply except where otherwise provided for in the Particular Specification, or where the Engineer may specifically direct a variation.

The Particular Specification referred to above will be incorporated in the Contract Documents for particular requirements of project.

The General Specification shall, except where superseded by the Particular Specification, be a part of Contract and shall be read in conjunction with the General Conditions of Contract, the Drawings, Bills of Quantities and other Contract Documents.

The Drawings on which the Contract is based shall be listed in the Particular Specification, and any notes or dimensions thereon shall take preference over this General Specification.

In this General Specification reference is made to the Standards issued by the American Society for Testing and Materials (ASTM), the British Standards Institution (B.S.), the Deutsche Normenausschuss (DIN), the Association Francaise ;de Normalization (AFNOR), and the International Organization for Standardization (ISO). Such references shall in every case be deemed to include the latest edition or issue of such Standards including all revisions issued up to the date of invitation to tender.

1.DEMOLITION WORKS

# .1.General Demolition:

1.1. 1 Scope:

All demolition work shall be completed as detailed including:

- demolition of designated existing constructions and/or structures completed including slabs and footings.

- Sealing if required of existing pipelines when not removed.

- Cutting into existing structures to accomplish interconnection of new work with existing and making good.

- Removal of existing protective coatings from surfaces to permit resurfacing, patching and re-coating of surfaces

- Arrange with affected utilities owners for renewal and/or relocation of their existing services.

- Removal of all mechanical and electrical equipment.

- Removal from site and disposal in a legal manner of debris and salvable and demolished materials without on-site accumulation thereof.

- Filling all voids and holes and making good all disturbed surfaces.

- Handling all flows.

- Protection of existing and new work from damage.

1. 1.2 Verification Conditions:

Prior to performance of demolition work, Contractor shall inspect the site and perform the following:

Thoroughly investigate on and off-site conditions and they affect work of this Section and determine type of structures, improvements, new construction schedule and priorities and applicable requirements of governing authorities.

Perform work in a fully coordinated manner with Work of other Contracts and/or other trades to assure completion without interference or delay to progress of the work.

1.1.3 Requirements:

Work shall be performed with sequence requirements agreed upon with the Engineer and shall where necessary assure uninterrupted traffic on the existing roads sewage flow in the pipes sewers or pump stations treatment works, etc.  Prior to commencing any particular demolition work, the Contractor shall submit in writing to the Engineer a detailed proposal including time sequence and the methods which he proposes to use for the particular demolition operation. Approvals by the Engineer of methods to be used in no way limits the responsibility of the Contractor  under any clause in any of the Specifications.

As specified, sewage flows must continue and the Contractor shall make all necessary arrangements to ensure that sewage flows are maintained in a safe manner.

Same is also is applicable to other utilities.

Precautions must therefore be taken to ensure that no damage is done to any facilities except those indicated on the Drawings and Specifications. The Contractor will be held responsible for any costs whatsoever involved in any damage which he has used to any work outside his Contract limits. The Contractor is not only responsible for the costs of any repairs to any structures built or under construction, but also for any other costs which are attributable to his actions.

1. 1.4 Pipes,  Utilities and Conduits:

The Contractor shall inform the Engineer 72 hours prior to the cutting of any pipes or conduits leading to demolition of manholes or form a structure to be demolished. All pipes, manholes or conduits which he locates and which are not shown on the Drawings shall be brought to the attention of the Engineer.

Pipes, conduits, utilities, etc. which are necessarily cut shall be either carefully or permanently capped or rerouted as indicated on the Drawings. Utility lines not specifically noted for disposition but which are encountered in the Work shall be capped, extended, protected, or reworked as necessary for completion of the work as directed by the Engineer.

1.1. 5 Debris Removal:

All rubble, debris and waste naturals generated during the demolition procedures shall be removed by the Contractor form the site as it accumulates.  The whole of the site occupied by the Contractor shall be kept in a clean and orderly state. The Contractor, at his own expense, shall find suitable dumping grounds for the waste materials and it shall be his responsibility to pay any costs whatsoever involved in securing the dumping grounds. The dumping ground site shall be approved by all relevant authorities. It is the Contractor’s responsibility to seek and obtain such approval and to file with the Owner copies of all approvals or agreements so obtained.

1.1.6 Protection:

The Contractor shall  take care to prevent spread of dust and flying particles, sprinkle rubbish and debris with water to keep dust to a minimum. maintain adequate fire protection, including extinguishers and operative water-house lines during demolition of inflammable portions of work. Provide temporary barricades, fences and safeguards to eliminate  hazards to persons and property without interference to use of adjacent property, public rights of way, utilities and structures.

1.1. 7 Completion:

The Contractor shall leave his work and the adjacent areas affected, free and clear from all debris caused by the work of this Section.  During and upon completion of work herein specified, the Contractor shall remove from building and site all debris, unused material and equipment  caused by work of this Section and leave Work in a clean, acceptable condition.

# 1.2removal, Reinstatement And/Or Relocation Of Obstructions, Pipelines, Pavement And Utilities

1.2.1 Scope:

This Work shall consist of the removal, reinstatement and/or relocation wholly or in part, temporarily or permanently,  and satisfactorily disposal of all existing utilities, fences, structures, abandoned pipelines and any other obstructions which are encountered during construction and not designated or permitted to remain, except for the obstruction to be demolished or removed and disposed of under other items in the Contract.  It shall also include the saving of designated materials and backfilling the resulting trenches, holes and pits.

When structures like pipes, tiles, trees etc. are to be removed only temporarily to excavate trenches or for similar works the Contractor shall take any possible measure to remove them without causing any damage and will provide for the reinstatement of the previous conditions to the satisfaction of the Engineer.

1.2.2  Construction Requirements

The Contractor shall raze, remove and dispose of all buildings and foundations structures fences and other obstruction any portions of which are on the right-of-way, except utilities and those for which other provisions have been made for removal.  All designated savable material shall be removed without unnecessary damage, in sections or pieces which may be readily transported, and shall be stored by the Contractor at specified spaces within the project limits. If approved by the Engineer materials that have to be restored on completion of the works may be left on site provided they are disposed to the satisfaction of the Engineer.  Unusable perishable material shall be destroyed.  Non-perishable material may be disposed of outside the limits of view from the project with written permission of the property owner on whose property the material is placed.  copies of all agreement with property owners are to be furnished to the Engineer.

Salvaged pipes culverts or other structures not to be restored shall be stored at designated and accessible points on the project as approved by the Engineer and shall be the property of the Employer.

1.2.3  Removal of Culverts, Other Drainage Structures

Culverts and other drainage structures in use by traffic shall not be removed until satisfactory arrangements have been made to accommodate traffic.

Unless otherwise directed, the substructures of existing structures shall be removed down to the natural stream bottom and those parts outside of the stream shall be removed thirty (30) centimeters below natural ground surface.

Blasting or other operation necessary for the removal of an existing structure or obstruction or obstruction, which may damage new construction shall be completed prior to placing the new work.

1.3Removal and Relocation of Pipes, Conduits etc.

1.3.1 Scope:

Pipes, conduits, utilities, etc., which necessarily cut shall be either permanently capped or rerouted as indicated on the Drawings.  Utility lines not specifically noted for disposition but which are encountered in the Work shall be capped, extended , protected or reworked and relocated as necessary for completion of the work as directed by the Engineer.

1.3.2 Relocation:

The relocation of the encountered utilities either shown on the Drawings or not shall be done by the Contractor at full satisfaction of the Engineer and in accordance with the recommendations of the relevant responsible Authority and the Contractor shall be held responsible for the satisfactory relocation and reinstatement of the working conditions of the encountered utilities.

The costs of this relocation shall not be paid directly but it shall be considered as subsidiary to the several paying items in the Bill of Quantities.

1.3.3  Removal:

Unless otherwise provided , all pipes which will not used any more, shall be carefully removed and every precaution taken to avoid breaking or damaging the pipe.  The Contractor  shall be held responsible in taking all the possible measures for the satisfactory removal of such structures in a usable condition.  The removed utilities shall become property or the Employer.

# 1.4Cleaning of Sewerage Structures to be Abandoned or Destined to Other Uses:

When septic tanks, cesspits, soak pits, manholes chambers, pumping station, sumps or other structures are encountered within the Contract limits and outside private properties and are to be abandoned, they shall be totally emptied and dislodged and all internal surfaces shall be thoroughly cleaned to the satisfaction of the Engineer.  The contents be disposed of offside by the Contractor to an approved tip.  The Contractor shall submit in writing to the Engineer his proposals for dislodging and cleaning.  If it is found on Site that his methods are unsatisfactory the Contractor shall immediately employ an improved method of dislodging and cleaning .  No structure scheduled to be demolished shall be broken out until the sludge within it has been totally removed .

The above cleaning shall not be paid directly but it shall be considered as subsidiary  to the several paying  items in the Bill of Quantities.

# 1.5Backfilling of Abandoned Structures

Upon receipt of the Engineer’s approval the base of the structure shall be punctured and the roof slab and tops of wall shall be broken out and this material used to partially fill the void.  The remaining void shall be filled with sand watered and well compacted up to the underside of the  cover slab. The manhole frames and covers shall be handed over as directed by the Engineer.

Where instructed by the Engineer to abandon only and not fully demolish a structure the Contractor shall fill the void with sand watered and well compacted up to the underside of the cover slab.  The manhole frames and covers shall be removed and handed over as directed by the Engineer, all  openings sealed with a concrete slab and the final surfaces reinstated in accordance with the Engineer’s instructions.

If an existing service is found in these structures the contractor shall bring this to the notice of the Engineer.  The Contractor shall carry out the instructions of the Engineer.  If a sleeve is to be provided to protect the service the sleeve shall extend 100 mm on either side of the structure.  When backfilling or working around an existing service or sleeve the Contractor shall take all precautions to ensure no damage is done.

The backfilling works shall not paid directly but it shall be considered as subsidiary to the several paying items in the Bill of Quantities.

# 1.6Abandonment of Existing Pipelines

The Engineer shall direct where existing sewers house connections and pumping mains are to be abandoned. Prior to proceeding the Contractor shall inform the Engineer in writing of his intention to commence abandonment and shall obtain his written approval.

Unless otherwise shown on the drawings or instructed by the Engineer all existing sewer and house connections to be abandoned shall be completely filled with a cement slurry or similar material using a grout pan or an alternative method approved by the Engineer by which the discharge slurry can be forced into the pipeline under pressure.

The Contractor shall be responsible for ensuring that all existing connections into the sewers to be abandoned have been either plugged or disconnected before filling proceeds.

Where  a sewer or house connection to be abandoned connects into a manhole or chamber to be retained the connection shall be plugged at the chamber wall and the associated channel in the benching of the manhole or chambers shall be thoroughly cleaned and filled with cement mortar.

Unless otherwise shown on the Drawings or instructed by the Engineer existing pumping mains to be abandoned shall be flushed out and sealed at each end of the pipeline with a removable expanding stopper to the approval of the Engineer.  Where chambers occur on the pipeline ends sealed as detailed above.

Existing pipelines other than sewers to be abandoned shall be sealed at each end of the pipeline with a removable expanding stopper to the approval of the Engineer.

The above works necessary for the abandonment of existing pipelines shall not be paid directly but it shall be considered as subsidiary to the several paying items in the Bill of Quantities.

# 1.7Demolition of existing Road Pavement

Removal of existing asphalt concrete road pavement shall be carried out at the location shown on the Drawings or as directed by the Engineer.

Pavement to be demolished and removed shall be only those clearly indicated in the Drawings and instructed by the Engineer; no pavement shall be removed without prior approval by the Engineer. Any pavement or surfacing existing in the roads to be paved under the provision of this Contract, shall be removed and the cost of this removal shall be considered subsidiary to other payment items in the Bill Quantities.

This demolishing operation shall be carried out in such manner as not to damage portions of other roads not required to be removed or any other joining property.

All the excavated material shall be loaded and hauled away to a dumping area approved by the relevant Authority.

# 1.8Removal of Side Walk, Concrete Paving:

Removal of existing sidewalk and concrete paving shall be carried out at the locations shown on the Drawing or as directed by the Engineer.

This operation shall be carried out in such manner as not to damage portions of sidewalk not required to be removed.

All the excavated material shall be loaded and hauled away to a dumping area approved by the relevant Authority.

# 1.9Reinstatement of Surfaces

When to execute the Works an existing paved surface (concrete or asphalt) has to be excavated, the contractor shall provide for the cutting of the same without causing any damage to the portion of surface not necessary to be cut.

When the excavation of the trench and the laying of the new sewers has been completed and all tests have been successfully carried out, the contractor shall provide for the reinstatement of the existing surface.

The concrete surfaces shall be reinstated with a minimum thickness of 15cm of concrete class B200 at the full satisfaction of the Engineer.

# 1.10Removal of Road Furniture

All existing road furniture (guard rails, guard post, road signs, advertisement signs, cat’s eyes, etc.) which removal is not paid under pay item present in the Bill of Quantities and which is ordered by the Engineer to be removed, shall be removed and disposed off by the contractor as per Engineer’s instruction.

Where so instructed by the Engineer these road furniture will be relocated within the limits of the contract at the same conditions of the one removed. The above removals and reinstatement shall not be paid directly but it shall be considered as subsidiary to the several paying items in the Bill of Quantities.

# 1.11Removal of Fence

The contractor shall take down existing fencing and gates including their foundation in the area shown on the drawings where new fence and gates shall be erected or wherever directed by the Engineer and it shall ensure the provision of suitable terminal posts, lengths of fencing or whatever is necessary to ensure the integrity of the remaining length of fencing.

Removed fence, gates posts and foundations shall be disposed off in a dumping area approved by  the relevant Authority unless the owner prescribed the fence, gates, posts and foundation to be salvaged in which case the said item shall be delivered to the store yards designated by the owner.

# 2. EXCAVATION  WORKS

This section covers, excavation, leveling, trenching and backfilling work and shall include the necessary clearing, grubbing and preparation of the site; removal and disposal of all debris; excavation and trenching as required; the handling, storage, transportation and disposal of all excavated material; all necessary sheeting, shoring and protection work; preparation of sub grades; pumping and dewatering as necessary or required; protection of adjacent property, backfilling, pipe embodiment, obstacles removal surfacing and grading and other related work.

No classification of excavated materials will be made.

# 2.1.Datum and Nature of Excavation

The datum for the Site shall be that shown on the Drawings. Information pertaining the nature of the ground may be given to the Contractor, when available, but the contractor has to verify correctness of existing ground level by him.

# 2.2. Site Preparation

Prior to commencing any excavation work, clearance from the concerned authorities must be obtained by the contractor, the Contractor shall establish a horizontal and vertical survey network to approved accuracy from the Engineer, record existing ground elevations. The Contractor shall prepare the site for construction by clearing, removing and disposing of all items not indicated on the Drawings to remain or so defined by the Engineer.

# 2.3. Existing Utilities

The Contractor shall ascertain the where about of all existing utilities on the site both, above and below ground.

Such utilities shall be removed, sealed or rerouted in a manner prescribed by the authorities concerned at the Contractor's own expense. The Contractor shall also be held responsible for all damages entailed on any of the utilities adjacent to the site resulting from the Works.

# 2.4. Removal of Existing Structures and Other Obstructions

This work shall include, but not be limited to, the removal of existing structures, trees, landscaping and other obstructions interfering with the Works. The salvaging of any of these materials for the use for the Employer shall be as directed by the Engineer and unwanted materials shall be disposed off the Site in a satisfactory manner at the Contractor's expense.

# 2.5. Cleaning and Grubbing

The Contractor shall perform the clearing and grubbing (if any), of top soil consisting mainly of loose soil, vegetable and organic matters, drift sand, unsuitable soil and rubbish by scarifying the areas to be excavated and sidewalks to a minimum depth of 300mm from the natural ground level. All materials resulting from the above operations shall be removed from the site, loaded and transported and off loaded, spread and leveled to approve dumps as directed by the Engineer.

During excavation, materials suitable for backfill and fill be stockpiled on the site at sufficient distance from the sides of the excavation to avoid over-loading and prevent cave-ins or mixing with the concrete during the construction of foundation.

# 2.6.Setting Out

Each structure or building and/or portion thereof shall be properly set out by the Contractor as shown on the Drawings and inspected and approved by the Engineer prior to commencing excavations. Locate and clearly flag trees and vegetation to remain or to be relocated.

Remove obstructions, trees, shrubs, grass, and other vegetation to permit installation of new construction. Removal includes digging out stumps and obstructions and grubbing roots.

1.	Do not remove trees, shrubs, and other vegetation indicated to remain or to be relocated.

2.	Cut minor roots and branches of trees indicated to remain in a clean and careful manner where such roots and branches obstruct installation of new construction.

3.	Completely remove stumps, roots, obstructions, and debris extending to a depth of 18 inches (450 mm) below exposed subgrade.

Fill depressions caused by clearing and grubbing operations with satisfactory soil material, unless further excavation or earthwork is indicated.

1.	Place fill material in horizontal layers not exceeding 8-inch (200-mm) loose depth, and compact each layer to a density equal to adjacent original ground.

# 2.7.Surface Leveling

All excavation on Site shall be complete before any fill is deposited. Excavations over areas of Site or filling with approved material shall be carried out where required to the levels shown on the Drawings or to such further levels as may be directed.

# 2.8.Size and Depth of Excavation

Excavations shall be cut to the size and taken down to the formation levels shown on the Drawings. Incase the contractor has exceeded the excavation depth beyond the formation level without the Engineer's written instruction, he shall fill up the part so excavated with Mass concrete as defined in Section 3, Concrete Works, at his own expense.

# 2.9.Shoring Excavation

The sides of excavations shall be supported as necessary to maintain a vertical face and/or to prevent caving-in of any nature, especially during subsequent operations.

The Contractor shall be responsible for the design, supply, fixing, safety and removal of all planking, strutting and shoring required to the side of the excavations. Excavations unshared near vertical or vertical sides shall be backfield without undue delay.

# 2.10.Types of Excavations

Excavations shall be classified according to the nature of the material to be removed either as excavation in rock or as excavation in earth.

Excavation in rock shall be defined as including all excavations in hard and consolidated materials which cannot be removed by normal excavators tools and equipment and which required drilling, blasting or other special means for their removal. All excavations, which are not rock, shall be defined as excavation in earth.

# 2.11.Lack of Required Bearing Capacity

The contractor has to verify the design bearing capacity at the formation level before initiating the foundation works at his own expense.

Where the required bearing capacity is not obtained at the formation level shown on the Drawings, the excavation shall be inspected or tested by the Engineer and upon his written instruction shall be extended to the depth and sizes he requires and filled into the original formation level with Mass concrete or other approved material as directed.

# 2.12.Preparation and Inspection of Excavations

All excavations shall be kept free of water arising from what sever source and shall be properly cleaned out from all loose and foreign matter, Leveled and named.

The Contractor is to report to the Engineer when excavations are ready for inspection and all excavations are to be approved before any further work is done.

# 2.13.Filling

The Engineer shall approve all filling materials before being placed in position. Approved earth, sand, concrete block, hard-core, clean broken brick, or other suitable material free from rubbish shall be used to make up levels as shown on the Drawings. The material shall be placed in successive layers each having a finished thickness not exceeding 25 cm, watered, well rammed with mechanical rammers and thoroughly compacted prior to the placement of the successive layer.

Any exposed sides or edges of fill shall be properly and evenly graded to a slope of 1 vertical in 3 horizontal or as otherwise directed or specified. When the required quantities of approved fill are not found on Site the Contractor shall obtain them from locations approved by the Engineer.

2.7.1	Soil Materials for different backfilling type

A.	General: Provide borrow soil materials when sufficient satisfactory soil materials are not available from excavations.

B.	Satisfactory Soils: ASTM D 2487 soil classification groups GW, GP, GM, SW, SP, and SM, or a combination of these group symbols; free of rock or gravel larger than 3 inches (75 mm) in any dimension, debris, waste, frozen materials, vegetation, and other deleterious matter.

C.	Unsatisfactory Soils: ASTM D 2487 soil classification groups GC, SC, ML, MH, CL, CH, OL, OH, and PT, or a combination of these group symbols.

1.	Unsatisfactory soils also include satisfactory soils not maintained within 2 percent of optimum moisture content at time of compaction.

D.	Backfill and Fill: Satisfactory soil materials.

E.	Subbase: Naturally or artificially graded mixture of natural or crushed gravel, crushed stone, and natural or crushed sand; ASTM D 2940; with at least 90 percent passing a 1-1/2- inch (38-mm) sieve and not more than 12 percent passing a No. 200 (0.075-mm) sieve.

F.	Base: Naturally or artificially graded mixture of natural or crushed gravel, crushed stone, and natural or crushed sand; ASTM D 2940; with at least 95 percent passing a 1-1/2-inch (38-mm) sieve and not more than 8 percent passing a No. 200 (0.075-mm) sieve.

G.	Bedding: Naturally or artificially graded mixture of natural or crushed gravel, crushed stone, and natural or crushed sand; ASTM D 2940; except with 100 percent passing a 1-inch (25-mm) sieve and not more than 8 percent passing a No. 200 (0.075-mm) sieve.

Place and compact backfill in excavations promptly, but not before completing the following:

1.	Construction below finish grade including, where applicable, dampproofing, waterproofing, and perimeter insulation.

2.	Surveying locations of underground utilities for record documents.

3.	Inspecting and testing underground utilities.

4.	Removing concrete formwork.

# 2.14Cutting Pavement and Surface Materials

The Contractor shall remove only as much of any existing pavement as is necessary for the prosecution of the work. The Engineer's Representative may require that the pavement be cut with pneumatic tools, without extra compensation to the Contractor, wherein the opinion of the Engineer's Representative it is necessary to prevent damage to the remaining road surface. Where pavement is removed in large pieces, it shall be disposed of before proceeding with the excavation.

From areas within which excavations are to be made, loam and topsoil shall be carefully removed and separately stored to be used again as directed; or if the Contractor prefers not to separate surface materials, he shall furnish, as directed, loam and topsoil at least equal in quantity and quality to that excavated.

# 2.15.Excavation & Preparation of Tender Formation

The Contractor in carrying out excavation for cable/ducts shall, where required, erect and maintain an approved type of temporary fencing around any work and shall provide fenced access ways across the trenches.

The Contractor shall ensure that all excavation and timbering is carried out in a careful manner, that it is rendered secure and safe, and that all measures necessary are taken to prevent the removal or falling in of material beyond the trench dimensions detailed. The Contractor shall maintain all timbering until the completion of the work to the satisfaction of the Engineer and shall promptly remove any material which has caved into the excavation.

The Engineer may direct the Contractor to protect his excavation with timbering where, in his opinion, such timbering is necessary to ensure the safety of the workmen, adjoining structures and work generally. Any action taken by the Engineer in this regard will in no way relieve the Contractor of any responsibility or liability under the Contract.

A clear space shall be left between the edge of the excavation and the inner toes of the spoil banks, to the approval of the Engineer.

No back-throwing whatever shall be allowed and all materials shall be brought to the surface and formed in heaps clear of the excavation

The material excavated in trenches shall, if unsuitable, be removed from site and shall be replaced with suitable material.

Unsuitable material shall include:

- Materials from swamps, marshes and bogs

- Materials susceptible to spontaneous combustion

- Stumps and perishable material

- Clays of liquid limit exceeding 40% and/or plasticity index exceeding 11%

- Excessively wet materials

All surplus and unsuitable excavated material shall be carted to the approved tip.

The bottom of the trench shall be accurately graded.  Care shall be taken not to excavate below the depths indicated.  Where rock is encountered, the rock shall be excavated to the required depth. Uneven surfaces of the bottom of trench shall be excavated 150mm deeper. Such depth in rock shall be backfilled with approved fill material and compacted as specified and/or as directed by the Engineer.

Whenever unsuitable soil, which in the opinion of the Engineer is to be removed, shall be removed to the depth required and the trench backfilled to the proper grade with approved fill material and compacted.

The width and depth of the trenches for electrical and telephone cables/ducts shall be as specified in the relative drawings or as ordered by the Engineer. Banks may be sloped or widened to facilitate placement of cables, but not the extent that will cause interference with other utilities and structures. No battering of trenches shall be allowed under existing carriageways, unless otherwise agreed by the Engineer.

# 2.16. Protection of Existing Services

- Where new cable/ducts are to be laid alongside, over or under the existing, the Contractor shall take care to interfere as little as possible with the existing services and connections thereto and any damage shall be repaired by the Contractor to the approval of the appropriate Authority or by appropriate Authority at the cost of the Contractor.

- The Contractor shall make all arrangements for protecting existing services and for temporarily diverting them to maintain the services without interruption.

- Existing services, pipes, mains, ducts, etc., exposed in trenches for new work shall be protected in accordance with the requirements of the relevant Authority before trenches are refilled.

- The Contractor shall lay cables, fittings, specials, etc., under hedges, fences, walls, etc., as necessary.

- Where hedges are damaged or destroyed the whole shall be restored and reinstated with shrubs of the same kind as the hedge, planted in due season in an approved manner and fenced on each side with post and rail stock proof fences finished on top with one strand of galvanized barbed wire, or otherwise protected as required by the owners or occupiers and the Engineer.

- Where fences or walls are damaged or destroyed the whole shall be restored and reinstated with like materials to the satisfaction of the owners or occupiers and the Engineer.

- The Contractor shall ensure that no trees are damaged or permanently removed in carrying out the Contract except where directed  due to the presence of permanent works

# 2.17. Backfilling of Trenches

- After the cables/ducts have been laid, the trench refilling shall commence with approved fill in compacted layers not exceeding 200 mm thick, each layer  being well compacted by hand with iron rammers weighing not less than 5 kg, until the trench has been filled to a height of 300 mm above the top of the cable/duct.

- The remainder of the trench shall then be refilled in compacted layers not exceeding 200 mm in thickness, each layer being well compacted with power rammers, vibrating plate compactors or other mechanical means of a type to be approved until the ground is thoroughly consolidated up to the required level for surface reinstatement. Each layer shall be compacted to 95% of its maximum dry density. Should the quantity of the excavated materials be not sufficient , due to unsuitability or otherwise, for the process of backfill and fill, the Contractor shall obtain the quantity required of such backfill and fill from approved borrow pits and transport same to the site of work at his own expense.

- Trenches shall not be backfilled until all required tests are performed and until the Engineer has verified that the cables etc have been installed in accordance with the specifications and drawings.

- Lumps and clods shall be broken up before use. Materials shall not be dropped from a height and where directed water shall be added to assist in adequate consolidation.

- Where cover to cables/ducts is less than 400mm, or where ordered by the Engineer, protection in the form of concrete encasing shall be provided according to an approved drawing or as ordered by the Engineer.

The Contractor shall not place backfill against or on structures until they have attained sufficient strength to support the loads (including construction loads) to which they will be subjected, without distortion, cracking or other damage as practicable after the structures are structurally adequate and other necessary work has been done, special leakage tests, if required, shall be made. Promptly after the completion of such tests, the backfilling shall be started and then shall proceed until its completion. The best of the excavated materials shall be used in backfilling, within 50cm of the structure. Unequal soil pressure shall be avoided by depositing the material evenly around the structure.

The material shall be placed and compacted as specified below, insofar as applicable. Compaction shall be accomplished by water-jetting or pudding, if the nature of the material permits, otherwise by tamping.

# 2.18.Disposal of Surplus Material

All surplus excavated material not used in backfilling or leveling shall be located and transported elsewhere on the site as required by the Engineer or, if not required on the site, shall be loaded and carted away from the site to a dump to be selected by the contractor and approved by the client and the Municipality.

All rubbish arising from the works shall be cleared away and removed from the Site as it accumulates and also on completion of the Works.

# 3. CONCRETE WORKS

# 3.1.Cement

The cement used shall be Portland Cement conforming in all respects ASTM standard Specification, C150, or to BS 12, except that bags shall contain 50kg net  1% and barrels or containers shall contain multiples thereof When The Particular Specification does not mention the typo or types desired, the requirements of Portland Cement C l50, Type 1 or of Ordinary Portland Cement BS 12, shall govern. If cements other than the above are required they shall be covered fully by the Particular Specification. The Contractor shall at all times furnish the Manufacturer's statement of the above Standard Specifications together with the date of manufacture, certified by an independent agency in the country of origin approved by the Chief Engineer.

The Cement shall be delivered to the Site by the Contractor in the original sealed and branded bags or containers of the manufacturer in batches not exceeding 100 tons and shall be stored in a proper manner off the ground to prevent deterioration. Each batch shall be stacked separately and used in the order of delivery. No cement shall be used which has been manufactured more than (12) months prior to its proposed use on Site.

All cements whether stored in bulk or in bags, barrels or containers in warehouses or on Site shall be sampled for testing according to ASTM C183. Test samples shall be taken at any time if so requested. Testing of cement shall be in accordance with the methods required by ASTM C150 and C 175 or BS 12.3.02

# 3.2.Aggregates

This specification covers fine and course aggregates other than lightweight aggregates for use in the production of concrete. When lightweight aggregates are required they shall be defined in the Particular Specification The aggregates shall be crushed gravel or stone, and shall comply with BS 882 for graded or single size aggregate and is to be obtained from approved source. For convenience, part of clauses of PS 822 (Grading) including Tables 1,2 and 3 is reproduced therein the use of the aggregates containing limestone is not permitted. The maximum size of aggregates shall not be larger than 1/5 of the narrowest dimension of the concrete element. Aggregate should be free from chalky materials.

## 3.2.1 Coarse Aggregate:

The grading of course aggregate, when analyzed by the method given for sieve analysis in BS 812 shall be within the limits given in Table 1.

TABLE 1. COARSE AGGREGATE

| BS 410 test sieve |  | Percentage by Weight Passing BS Sieves |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal Size of Normal Size of Graded Aggregate Single-Sized Aggregate |  |  |  |  |  |  |  |
|  |  | 38-5mm 1½ to 3/16" | 19-5mm 3/4 to 3/16" | 13-5 mm 11/2-3/6" | 64mm 2 ½" | 38 mm 1 ½% | 19mm 11/2" | 13mm 11/2” | 10mm 3/8" |
| Mm | In |  |  |  |  |  |  |  |  |
| 76.20 | 3 | 100 | - | - | - | - | - | 100 | 100 |
| 63.50 | 2 ½ |  | - | - | 100 | 100 | - | 85-100 | 85-100 |
| 38.10 | 1 ½ | 95-100 | - | 0-100 | 35-100 | 35-100 | 100 | 0-45 | 0-20 |
| 19.05 | 34 | 30-70 | - | 90-100 | - | 0-20 | 85-100 | 0-10 | - |
| 12.07 | ½ | - | 95-10 | 40-385 | 0-20 | - | - | - | 0-20 |
| 9.52 | 3/8 | 10-350 | - | 0-10 | - | 0-5 | 0-20 | - | - |
| 4.76 | 3/16 | 0-5 | 25-55 | - | - | - | - | - | - |
| Mm | No. |  |  |  |  |  |  |  |  |
| 2.40 | 7 | - | 0-10 | - | - | - | - | - | - |

## 3.2.2 Fine Aggregate.

The grading of a fine aggregate, when analyzed by the method of sieve analysis described m BS 812, shall be within the limits of one of the grading zones given in Table 2, except that a total tolerance of up to 5 percent may be applied to the percentages underlined. This tolerance may be split up; for example, it could be 1 percent on each of three sieves and 1 percent on another. The fine aggregate shall be described as fine aggregate of the grading zone into which it falls, e.g. BS 882, Grading Zone 1.

NOTES: It is intended that individual zones should not be specified in contract documents relating to concrete but that the concrete mixes should be modified to make the best use of the materials readily available.

TABLE 2, FINE AGGREGATE

| BS 410 test sieve |  | Percentage by Weight Passing BS sieves |  |  |  |
| --- | --- | --- | --- | --- | --- |
| mm | In | Grading | Grading | Grading | Grading |
| 9.52 | 3/8 | Zone 1. | Zone 2. | Zone 3. | Zone 4. |
| 4.76 | 3/16 | 100 | 100 | 100 | 100 |
| mm | No. | 90-100 | 90-100 | 90-100 | 95-100 |
| 2.40 | 7 | 60-95 | 75-100 | 85-100 | 95-100 |
| 1.20 | 14 | 30-70 | 55-90 | 75-100 | 90-100 |
| M |  |  |  |  |  |
| 600 | 25 | 15-34 | 35-59 | 60-79 | 80-100 |
| M.O.H |  |  |  |  |  |
| 300 | 52 | 5-20 | 8-30 | 12-40 | 15-50 |
| 150 | 100 | 0-10 | 0-10 | 0-10 | 0-15 |

# 3.3.Handling Aggregates

The choice and preparation of sites for stockpiling of aggregates, the number and sizes of stockpiles and the methods adopted to prevent segregation of component sizes shall be agreed with the Engineer. Course aggregate shall stockpiled in three separate grading 38-19 mm (11/2-3/4 in), 19-10 mm (3/4-3/8 in), 10-5 mm (3/8-3/16 in). When bulkheads shall separate stockpiles.

Stockpiles are to be on concrete or other and surface sufficiently sloped so that water is not retained in the base of the stockpiles. All aggregates are to be handled from the stockpile in such a manner as to secure a typical grading of the material, care being taken to avoid crushing the aggregates and contamination with extraneous matter.

Aggregates need not be stockpiled when a crushing-screening plant is used in tandem a bathing plant properly equipped with several bins for different sized aggregates having the appropriate weighing scales at each bin such that a mix of the desired graduation is obtained consistently and the whole operation is conducted to the satisfaction of the Engineer.

# 3.4.Water

Unless otherwise authorized in writing by the Engineer, only water from potable supply system of Gaza may be used for mixing concrete and other products containing cement. Similarly only potable water may be used for curing concrete and cement products during the first twenty-four (24) hours after pouring. Later, fresh water, or other water containing not more than 4750 PPM dissolved solids of which not more than 1000 PPM may be chloride, may be used for curing.

# 3.5.Quality of Concrete

Concrete shall be a mixture of cement, aggregates and water. Where air-entertainment is required, the method to be used shall be specified in the Particular Specification.  The mix proportions, workability and strengths of the various types shall conform to Table 3.1. The terms contained in Table 3.1 are defined as follows:

Water/Cement Ratio: The term water/cement ratio means the ratio by weight of the water to the cement in the mix, expressed as a decimal fraction. The water is that which is free to combine with the cement in the mix. This includes free water in the aggregate but excludes water absorbed or to be absorbed by the aggregate. The aggregate for this purpose shall be taken in a saturated surface-dry condition. The absorption of the aggregates shall be determined in accordance with BS 812.

TABLE 3.1.General Requirements For Type Of Concrete

| Type of Concrete | A-(B350) | B-(B300) | C-(B250) |
| --- | --- | --- | --- |
| Water/Cement Ratio | 0.40-0.45 | 0.45-0.50 | 0.50-0.55 |
| Aggregate/Cement Ratio | 5.0-5.5 | 5.5-6.5 | 6.5-7.5 |
| Fine &Total Aggregate Ratio | 35%40% | 35%-40% | 25%-40% |
| Cement, kg/m3 of Concrete | 400-450 | 300-400 | 300-350 |
| Slump, max. in cm | 5 | 7 | 9 |
| Preliminary Test Cubes, min | 305 | 260 | 220 |
| Compr. Strength at 7 |  |  |  |
| Days kg/cm2 |  |  |  |
| Works Test Cubes ruin, compr. Strength at 28 days | 405 | 345 | 290 |
| Kg/cm2 |  |  |  |
| Method of Compaction of | Vibrated | Vibrated | Vibrated |
| Concrete when placed. |  |  |  |

- The strength specified is for ordinary Portland cement BS 12 or Type 1 Cement to ASTM C 150, if other types of cement are specified, the required strength shall be defined in the Particular Specification.

- In case cylinders are used for determination of concrete compressive strength in accordance with ASTM 39, the corresponding shall be obtained by using a multiplication factor of 1.2.

Aggregate/Cement Ratio: The term aggregate/cement ratio means the ratio by weight of aggregate to cement in the mix. For this purpose the aggregate is taken

In a saturated surface-dry condition as for the water/cement ratio above.

Fine/Total Aggregate Ratio: The term fine total aggregate ratio means the ratio by weight of the fine aggregate to the total aggregate in the mix expressed as a

Percentage. For this purpose the aggregate is also taken in a saturated surface-dry condition as for the water/cement ratio above.

Volume of Air Entrained: The air content expressed as a percentage by volume of concrete, shall be determined by ASTM method C231 "Air Content of Freshly Mixed concrete by the Pressure Method”. At least one test for each 120 cubic meters of concrete shall be made.

Slump: The slump of the freshly mixed concrete shall be determined in accordance with Part 2 of BS 1881 or ASTM C 143. At least one morning and one afternoon test shall be made and whenever directed by the Engineer.

Strength of Concrete: Preliminary Test Cubes shall be taken from the trial mixes designed to select the job mix and shall be made and tested in accordance with Parts 6 and 8 of BS 1881. Works Test Cubes shall be those used for control during construction and shall be made and tested in accordance with parts 7 and 8 of BS 1881.

# 3.6.Adjustment of Mix Proportions

The Contractor when tendering having knowledge of the source and type of cement, aggregates, plant and method of placing he intends to use shall allow for the aggregate/cement ratio and water/cement ratio which he considers will achieve the strength requirements specified and will produce a workability which will enable the concrete to be properly compacted to its full depth and finished to dimensions and within the tolerances shown on the Drawings and required by the Particular Specification. In any event the aggregate/cement ratio and the water/cement ratio shall not exceed the upper limits specified in Table 3.1 above for each type of concrete. Furthermore, the quantity of cement per cubic meter of concrete shall in no case be less than the minimum specified in Table 3.1 above.

As soon as possible after signature of the Contract, the Contractor shall prepare such trial mixes as required to satisfy the Engineer that the specified concrete strengths will be obtained using the materials and mix proportions in accordance with the above clauses. The proportions of cement shall be increased if necessary to obtain the strengths required. From each trial mix, six Preliminary Test Cubes shall be made and tested two at 7 days and four at 28 days, the test at 7 days being intends to give an early indication of possible variation form the required strength. If the difference between the highest and lowest test results from any one trial mix is more than 15 percent of the average of the strength test results, the test is to be discarded and further trial mix made, unless all test results so obtained are above the required strength. Separate trial mixes are required for each type of concrete. The trial mix or mixes agreed by the Engineer shall be designated job mixes and used as a basis for actual concrete production.

# 3.7.Batching and mixing of Concrete

All concrete shall be batches by weight and mixed mechanically. Hand mixing shall not be allowed only upon the written permission of the Engineer. Concrete may both be batched and mixed on Site or outside the Site and transported thereto. When mixed outside the Site and transported to it. Batching and mixing shall be in accordance with ASTM Specification C 94 "Standard Specification for Ready-Mixed concrete".

When mixed on Site, batching and mixing shall be as follows:

Batching by Weight: The cement and each size of aggregate shall be measured by weight. Weight or volume may measure the water. The weight-batching machines used shall be of a type approved by the Engineer and shall be kept in good condition while in use on the Works. Checks are to be made as required by the Engineer to determine that the weighing devices are registering correctly.

Batching Aggregate by Volume: When batching aggregates by volume is allowed, as and when required, the cement shall be batched by weight and the water by weight or volume. Each size of aggregate shall be measured in metallic containers the depth of which is at least equal to their greatest width. The containers shall be of such shape that their volume can be easily checked by measurement. Mixing Concrete: The location of the batching and mixing plant shall be agreed with the Engineer. Concrete shall be mixed in a batch mixer of a type approved by the Engineer and in good condition having a drum rotating about a horizontal or inclined axis. Continuous mixer shall not be used. Each mixer is to be fitted with a water-measuring device having an accuracy within one percent (1%) of the quantity of water required for the batch. The water-measuring device shall be such that its accuracy is not affected by variations in the water supply pressure.

The batch shall be so charged into the mixer that some water (about 10%) enters the drum in advance of the cement and aggregates. Water shall then be added gradually while the drum is in motion such that all required water shall be in the drum by the end of the first quarter of mixing time. The concrete shall be mixed until a mixture of uniform color and consistency is obtained. Where double-drum, high performance mixers of a type approved by the Engineer are used, a minimum mixing time of 70 sec. may be allowed. The amount of concrete mixed in any one batch is not to exceed the rated capacity of the mixer. The whole of the batch is to be removed before materials for a fresh batch enter the drum. On cessation of work, including all stoppages exceeding 20 minutes, the mixers and all handling plant shall be washed with clean mixing water. If old concrete deposits remain in the mixer drum, it shall be rotated with clean aggregate and water prior to production of new concrete. Concrete mixed as above is not to be modified by the addition of water or in any manner to facilitate handling or for any other reason.

# 3.8.Prescribed mixes for ordinary structural concrete

Weights of cement and total dry aggregates in kg produce approximately one cubic meter of fully compacted concrete together with percentages by weight of fine aggregate in total dry aggregates.

## Table 3.2

|  | Nominal Max. Size of | 40 |  | 20 |  | 14 |  | 10 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Concrete | Aggregate (mm) |  |  |  |  |  |  |  |  |  |
| Grade | Workability | Medium | High | Medium | High | Medium | High | Medium | High |  |
|  | Limits to slump that | 50-100 | 100-150 | 25-75 | 75-125 | 10-50 | 50-100 | 10-25 | 25-50 |  |
|  | may be expected |  |  |  |  |  |  |  |  |  |
|  | (mm) |  |  |  |  |  |  |  |  |  |
| 7 | Cement (kg) | 180 | 200 | 210 | 230 | - | - | - | - |  |
|  | Total aggregate(kg) | 1950 | 1850 | 1900 | 1300 | - | - | - | - |  |
|  | Fine aggregate(%) | 30-45 | 30-45 | 35-50 | 35-50 | - | - | - | - |  |
| 10 | Cement(kg) | 210 | 230 | 240 | 260 | - | - | - | - |  |
|  | Total aggregate (kg) | 1900 | 1850 | 1850 | 1800 | - |  |  |  |  |
|  | Fine aggregate(%) | 3045 | 3045 | 35-50 | 35-50 | - | - | - | - |  |
| 15 | Cement (kg) | 250 | 270 | 280 | 310 | - | - | - | - |  |
|  | Total aggregate (kg) | 1850 | 1800 | 1800 | 1750 | - | - | - | - |  |
|  | Fine aggregate(04) | 3045 | 3045 | 35-50 | 35-50 | - | - | - | - |  |
| 20 | Cement (kg) | 3(10 | 320 | 320 | 350 | 340 | 380 | 360 | 410 |  |
|  | Total aggregate (kg) | 1850 | 1750 | 1800 | 1750 | 1750 | 1700 | 1750 | 1650 |  |
|  | Sand * |  |  |  |  |  |  |  |  |  |
|  | Zone 1 (%) | 35 | 40 | 40 | 45 | 45 | 50 | 50 | 55 |  |
|  | Zone 2 (%) | 30 | 35 | 35 | 40 | 40 | 45 | 45 | 50 |  |
|  | Zone 3 (%) | 30 | 30 | 30 | 35 | 35 | 40 | 40 | 45 |  |
| 25 | Cement (kg) | 340 | 360 | 360 | 390 | 380 | 420 | 400 | 450 |  |
|  | Fatal aggregate (kg) | 1800 | 1750 | 1750 | 1700 | 1700 | 1650 | 1700 | 1600 |  |
|  | Sand * |  |  |  |  |  |  |  |  |  |
|  | Zone 1 (%) | 35 | 40 | 40 | 45 | 45 | 50 | 50 | 55 |  |
|  | Zone 2 (%) | 30 | 35 | 35 | 40 | 40 | 45 | 45 | 50 |  |
|  | Zone 3 (%) | 30 | 30 | 30 | 35 | 35 | 40 | 40 | 45 |  |
| 30 | Cement (kg) | 37(1 | 390 | 4(10 | 430 | 430 | 470 | 460 | 510 |  |
|  | Total aggregate (kg) | 1750 | 1700 | 1700 | 1650 | 1700 | 1600 | 1650 | 1550 |  |
|  | Sand * |  |  |  |  |  |  |  |  |  |
|  | Zone 1 (%) | 35 | 40 | 40 | 45 | 45 | 50 | 50 | 55 |  |
|  | Zone 2 (%) | 30 | 35 | 35 | 40 | 40 | 45 | 45 | 40 |  |
|  | Zone 3 (%) | 30 | 30 | 30 | 35 | 35 | 40 | 40 | 45 |  |

*  Sand is fine aggregate resulting from the natural disintegration of rock.

# 3.9. Work in Cold or Hot Weather

Concrete is not to be mixed or placed at a shade air temperature below 2 C on a falling thermometer or at a shade air temperature below 3 C on a falling thermometer. When the shade air temperature is 37 C and arising, special precautions shall be taken during concreting operations, such as shading of the aggregates and plant, cooling of the mixing water or other methods approved by the Engineer, so that the temperature of the concrete when placed shall not be in excess of 39 C. Fresh concrete placed at these temperatures shall be shaded from the direct rays of the sun to the satisfaction of the Engineer for a period of at least 24 hours. Concrete. Is not to be mixed and placed when the shade air temperature is 43 C or above.

# 3.10.Reinforcement

Steel reinforcement shall generally be one of the following types:

Mild, medium or high tensile smooth round bars complying with B S.  785 or similar approved standard.

Deformed, plain and clean billet steel bars for concrete reinforcement according to ASTM A615M-93.

Cold twisted bars complying with BS 1144 or similar approved standard.

In case any other type of reinforcement such as deformed bars or steel fabric is called for, it shall comply with the requirements of the Particular specification.

When the type and grade of steel reinforcement are not specified, the requirements for mild steel having a yield point of at least 2200 kg/cm2 and an ultimate tensile strength of 3500-5000 kg/cm2 shall govern, and for cold twisted bars having a theoretical yield point at 0.20% elongation of at least 4000 kg/cm2 and an ultimate tensile strength of at least 5000 kg/cm2. Manufacturers test certificates for all classes of reinforcement shall be supplied when required. Specimens sufficient for three tensile test and three cold bending tests per ten tons of bars or fraction thereof and for each different size of bar shall be sampled under the supervision of the Engineer. Testing shall be in accordance with BS 785 or other approved standard and batches shall be rejected if the average results for each batch are not in accordance with the specifications.

All steel is to be totally free from dirt, paint, loose rust or scale when in position ready for concreting. The bars are to be accurately bent to the shapes indicated, and the bending must, whenever possible, be completed before the steel is fixed in position. Straight portions of bars must be time and bends must be kept out of winding. The internal radius of bends shall in no case be less than four times the diameter of the bar, except for stirrups, column binders, and wall shear bars which are to be bent to fit closely round the main bars. Great care is to be taken to bend stirrups, column binders, and wall shear bars, which are to be bent to fit closely around the main bars. Great care is to be taken to bend stirrups and binders separately and to sizes shown. In the absence of reinforcement bending schedules the bending requirements of B S. 1478 "Bending Dimensions of Bars for Concrete Reinforcement" or other similar approved standard shall govern. Except as otherwise allowed by the Engineer, bars are to be bent cold. Lengthening of bars by welding, and rebinding of incorrectly bent bars will not be permitted, except where requested by the Engineer. Unless otherwise allowed of in the Particular Specification splices in reinforcing bars shall be formed by lapping. Such laps in bars in any member shall be staggered. Except as otherwise indicated on the Drawings, the minimum overlap of lapped splices shall be 40 bar diameters or 30 cm. whichever is greater. Mixing of mid steel and H.T. is not allowable. Special steel for pre stressed concrete to be specified in the Particular Specification. The steel is to be fixed in position exactly as indicated, and the bars are to be securely wired together with 1.6 or 1.4 mm soft iron wire or approved spring steel clips wherever necessary to prevent any displacement during concerning. Spacers, chairs and the like, temporary or permanent are to be used as required to ensure that the steel has the exact amount of cover indicated. No permanent spacers may be shown on a surface where a fair-faced concrete finish or brushed aggregate finishes are required. Unless otherwise indicated, the minimum cover to the reinforcing bars is to be as follows:

# 3.11Minimum Cover

Position mm

- Main bars in external faces of columns and beams 25

- Main bars in internal faces of columns and beams 25

- Main bars in floor slabs and sophist of roof slabs 20

- Main bars in top of roof slabs 25

- Outermost bars in internal faces of walls 25

- Outermost bars in external faces of wall 25

- Bars in top of ground slabs 20

- Bars near faces in contact with soil 50

The placing of all reinforcement will be checked by the Engineer and in no case is concrete to be poured around any steel that has not been passed by him. The Contractor is to ensure that no steel is displaced from its position during the placement of concrete and until the concrete has set.

The insertion of bars into or removal of bars from concrete already placed will not be permitted. Reinforcement temporary left projecting from the concrete at the joints shall not be bent without the prior approval of the Engineer. Secondary reinforced concrete members for which no reinforcement details are given in the Drawings or the Particular Specifications shall have a minimum ratio of reinforcement area to concrete area of half percent (0.5%) The Contractor shall supply, design, erect, strike and remove the framework and be entirely responsible for its stability and safety so that it will carry the wet concrete and all incidental loading and preserve it from damage and distortion during its placing, vibration, ramming, setting and curing. It shall be so constructed as to leave the finished concrete to the dimensions shown on the drawings and of a material capable of providing the surface finish specified. In any event, the maximum permissible deflection under all loads shall not exceed 2 mm or 1/600 of the free span, whichever is less. Formwork shall be constructed as to prevent the loss of any liquid from the west concrete, and to be removable without shock to the partially set concrete. Then the concrete is to be vibrated, all wedges must be nailed so as to prevent slipping or distortion.

# 3.12.Formwork for Concrete

-	The Contractor shall obtain in advance of formwork fixing the approval of the methods and materials proposed.

-	Details of formwork for special finishes shall be approved before materials are ordered. Formwork shall provide concrete of the shape, lines and dimensions shown on the drawings in any case the maximum acceptable deflection will be not more than 1/600 of the span.

-	Formwork shall be constructed from materials of sufficient strength, supported to provide rigidity, curing, placing and compacting of the concrete.

-	Formwork panels shall have true edges for accurate alignment and shall be fixed with either vertical or horizontal joints.

-	Joints shall not permit leakage of grout, nor steps and ridges in exposed surfaces.

-         Rough formwork shall be bull-jointed, seasoned, sawn temper.

-        Fair formwork shall be used for all services required serviceability, structural   soundness and appearance. This finish shall be obtained from forms designed to proceed a hard smooth structure with true, clean arises. All surface blemishes shall then be filled with a fresh, specially prepared cement and fine aggregate paste whilst the concrete is still green where possible. After the concrete has been properly cured, the faces shall be rubbed down, if required, to procure a smooth surface. If the surface is to be exposed in the final work, every effort shall be made to match the color of the concrete. The angles

Of fair faced insitu concrete shall be produced with chamfers 2x2cm or as directed by the Engineer.

-	Formwork and supports shall be cleaned, temporary openings shall be provided for the removal of rubbish. The formwork shall be coated with an approved release agent and the excess removed. Release agent shall not be allowed to come into contact with concrete already placed or with reinforcement steel.

Not less than 24 hours notice shall be given for the inspection and approval of the formwork and reinforcement, prior to which concrete shall be poured. The Engineer's approval, however, does not relive the contractor from his contractual responsibility.

- Formwork shall be removed without damages to the concrete but not until the concrete has sufficient strength to support itself. Centers and props may be removed when the member has sufficient strength to carry itself and any loading within a reasonable factor of safety.

- External loading shall not be applied until the concrete has reached 28 days.

The Engineer should in accordance with the following table or as direct minimum periods in days for striking other formwork.

| Description - Columns - Beams, sides - Beams, soffit - Walls - Suspended slabs, soffit | Time For Removal 48 hours 48 hours 14 days in summer and 21 days in winter. 4 days 14 days in summer and 21 days in winter. |
| --- | --- |

Formwork, shuttering, props, or any other means of temporary or semi-permanent support shall not be removed from the concrete until the concrete is sufficiently strong to carry safely the load (dead and temporary). The Contractor shall inform the Engineer when he is ready to strike the formwork, or remove any form of temporary support, and shall obtain his written consent before proceeding. Any work showing signs of damage through premature loading is to be entirely reconstructed at the Contractor's expense.

The Contractor shall confirm positions and details of all

a) Permanent fixings

b) Pipes and conduit

c) Holes and chases to ensure that alterations are not made without the

Knowledge and approval of the Engineer.

The Contractor shall fix inserts or box out as required to correct positions before placing concrete, and shall form all holes and chases.  He shall not cut hardened concrete without approval.

# 3.13.Joints

Expansion joints shall be formed in the positions indicated and to the details shown on the Drawings or otherwise ordered by the Engineer. The expansion joints shall be filled with bitumen impregnated fiberboard to its full depth and width. The filling will be permitted to be used as permanent formwork only for the second casting. Where the fiberboard is exposed, it shall be cut back for a depth of at least 1cm. from the chamfered edges, filled and pointed with a resilient liquid polysuiphide polymenr sealant. Whenever the placing of the concrete is discontinued other than at the expansion faces, this discontinuity shall form a construction joint. Construction joints are to be made only along a horizontal or vertical plane except that in the case of inclined or curved members they shall be at right angles to the principal axis. Care shall be taken to prevent offsetting of the joint and to ensure water tightness. The joints shall in every way satisfy the requirements of the Engineer, and be in accordance with the Drawings.

Unless otherwise shown on the Drawings, construction joints will not be allowed in the supported portion slabs, beams and beam like members. At construction joints the Latinate film and porous layer of the already set concrete shall be removed and the surface keyed by hacking and then wire-brushed and thoroughly cleaned. Immediately before adding the new concrete, the surface it to be thoroughly wetted and a 1-cm thick coating of a fresh cement/sand mortar (having the same proportion of cement/sand as concrete in the mix) applied to the surface. The new concrete is then to be well compacted into the old.

The number of construction joints should be kept as few as possible consistent with reasonable precautions against shrinkage. Concreting should be carried out continuously up to construction joints.

Where it is necessary to introduce construction joints, careful consideration should be given to their exact location, which should be indicated on the drawings.

# 3.14.Placing

Concrete shall be conveyed from the mixer to its final position in any suitable manner, provided there is no segregation, loss of ingredients or contamination. It shall be placed in its final position before initial setting takes place and within 20 minutes of the addition of the water to the mixer. However, when agitating equipment is used to convey concrete such as in ready-mixed concrete, the elapsed time between the addition of the water and placing may be increased to 45 minutes The order of placing concrete shall be such as to prevent water from collecting at the ends, corners and along the faces of forms. It shall not be placed in large quantities at a given point and allowed to run or be worked over along distance in the form.

In any case, use of rake will be strictly avoided whenever possible, concrete shall be placed and compacted in even layers with each batch adjoining the previous one. The thickness of the layers shall be between 15 and 30 cm for reinforced concrete and up to 45 cm for plain (non-reinforced) concrete, the thickness depending on the width of forms, the amount of reinforcement and the need to place each layer before the previous one stiffens.

Concrete shall not be allowed to drop freely for more than 150 cm. To convey the concrete as near as possible to its final position, drop chutes of rubber or metal shall be used for small sections and bottom dump buckets or other suitable vessels for large sections. Concrete shall be carefully compacted when placed to ensure a dense and uniform mass free from air holes and cavities. Concrete types "A”, "B" and "C" shall be compacted by vibration, whereas type "D" and Mass Concrete may be vibrated or rammed, tamped and rodded. Mechanical or Electro-mechanical vibrators shall perform vibration. The vibrators shall be of the pluger (poker) type for insertion in the concrete except that plate type vibrators (external) shall be used if so required by the Engineer. The plunger type vibrators shall have a diameter compatible with the spacing of reinforcement, a sufficiently high frequency and handled by experienced personnel. They shall be immersed at regular intervals close enough to vibrate all of the concrete, but not too close to affect previously vibrated and partially set concrete. Each immersion shall continue until shortly after air bubbles cease to appear on the surface of the concrete, but shall not last more than 30 seconds. The vibrators shall be withdrawn gradually and vertically to ensure that no air pockets are formed. When external vibrators are used as directed by the Engineer, they shall be clamped to the forms whenever possible to avoid large impact during handling and the forms shall be so constructed as to withstand the additional vibrations. All vibrations, compaction and finishing operations shall be completed within 15 minutes from the time of placing the concrete in its final position. Workers shall not be allowed to walk over freshly placed concrete until it has hardened sufficiently to carry weight without distortion. Concreting of any one part or section of the work shall be carried out in one continuous operation, and no interruption of concerning work will be allowed without the approval of the Engineer. Where beams and slabs together form an integral part of the structure, they shall be poured in one operation, unless provision is made to form a construction joint. A record is to be kept by the Contractor on Site of the time and date of placing the concrete in each portion of the Works and the number and identification of the Works Test Cubes corresponding to these portions. Such records are to be handed to the Engineer weekly during the progress of the work. If placing of concrete by pumping is required it shall be specified in the Particular Specification.

Release agents for formwork should be carefully chosen for the particular conditions they are required to fulfill.  Where a concrete surface is to be permanently exposed only one agent should be used throughout the entire area. Release agents should be applied evenly and contact with reinforcement and prostrating tendons avoided.  Where the surface is to receive an applied finish care should be taken to ensure the compatibility of the release agent with the finish.

# 3.15.Admixtures

No admixtures. Of any type shall be used in the preparation of concrete or- concrete products unless so required by the Particular Specification or unless so directed by the Engineer. In case any such admixtures are used the rates and methods of application shall be strictly in accordance with the manufacturer's instructions.

# 3.16.Curing

Freshly placed concrete shall be protected from rain, dust storms, chemical attack, and the harmful effects of heat, wind, flowing water, vibrations and shocks. This protection shall continue until the concrete is sufficiently set such that it is no longer damaged by these factors. The Engineer shall determine when the protection is no longer required, but in any case this shall not be less than 24 hours after the time of placing.

Concrete shall be cured for at least seven days and as requested by the Engineer. Curing shall be effected by the direct application of water to the surface of the concrete or by other approved curing methods or curing compounds applied in accordance with the manufacturer's specifications. In case the application of such curing compounds is delayed for any reason, the concrete shall be kept moist until the application is made. Timber formwork covering the concrete shall be moistened with water at frequent intervals to keep it from drying during the curing period. Metal formwork exposed to the sun must be shaded from its direct rays, painted white or otherwise protected during the curing period.

# 3.17.Fair-Faced Finish

All fair-faced concrete shall be free from honeycombing and any defects arising from faulty form work or other causes. No patching up of any kind shall be allowed upon the removal of the forms except with the full knowledge and approval of the Engineer.

# 3.18.Other Types of Concrete

When other types of concrete. Such as pre stressed concrete or pre-cast concrete is required it shall be fully specified in the Particular Specification.

# 3.19.Testing

Prior to commencing the work, the Contractor, shall make available on site the following Minimum approved equipment kept in good condition at all times:

- Six 15cm cube moulds.

- Slump cones.

- Set of BS sieves or equivalent.

- Balance.

- Thermometer.

- Plastic Cylinder.

Other accessories as hand shovels, buckets, water, plastic cover, fabric cover, etc.

A water tank 3x2x0.8 m with the required piping and cover will be provided in the immediate proximity of the site office. As directed by the Engineer.

All testing shall be done in the presence of the Engineer or his authorized representative either on Site or in an approved testing laboratory as directed. The frequency of testing shall be as noted in the clauses of this Section and whenever required by the Engineer. The Works Test Cubes shall be made as follows for types "A", "B" and "C" concrete, whichever is more frequent:

a) At least three times weekly per mixing plant.

b) At least once for each individual part of the structure.

c) At least once per 100 cubic meters of concrete.

For type "D" and Mass concrete the rate shall be once per each 100 cubic meters of fraction they’re of. At least six cubes shall be made at one time. Two of the six cubes are to be tested at seven (7) days. The remaining four cubes are to be tested at 28 days, and their average strength must not fail below the minimum strength specified for each type of concrete and the lowest test result shall not be more than 15% below the average of the four cubes. When the result of the seven-day test is unsatisfactory', the Contractor may elect to remove and repeal ace the defective concrete without waiting for the 28-days test. If the result of the 28-days test is unsatisfactory, all concerning shall be stopped at the Contractor's expense and shall not proceed further without the written permission of the Engineer.

The Contractor shall then, in accordance with the instructions of the Engineer, remove cores and test same or conduct in-situ-load tests from or on suspect portions of the works, under the supervision of the Engineer, Concrete judged by the Engineer to be defective shall forthwith cut out, removed and replaced by the Contractor at his own expense. In the event of strengths consistently higher than those specified being obtained, the Engineer may authorize a reduction in the number of tests.

(Test at 7 days must not be less than 75% of the required strength at 28 days).

# 3.20.Protection.

High quality surface finishes are susceptible to subsequent damage and special protection must be provided in vulnerable areas.

Surface finishes from formwork or moulds:

Type A finish. This finish is obtained by the use of properly designed formwork or moulds of closely jointed sawn boards. The surfaces will be imprinted with the grain of the sawn boards and their joints.  In addition, small blemishes caused by entrapped air or water may be expected, but the surface should be free from voids, honeycombing, or other large blemishes.

Type B finish. The finish is obtained by the use of properly designed forms of closely jointed wrought boards. The surfaces will be imprinted with the slight grain of the wrought boards and their joints. Alternatively, steel or other suitable material may he used for the forms. Small blemishes caused by entrapped air or water may be expected, but the surface should be free from voids, honeycombing, or other large blemishes.

It should be note that finishes of Type A and Type B do not necessarily provide a suitable surface to receive in situ concrete or applied finishes, nor do they include special board-marked finishes.  Consideration should be given to the type of connection, or applied finish, and if necessary other types of treatment should be specified for the appropriate faces.

Type C finish.  This finish can only be achieved by the use of high quality concrete and by using properly designed forms having a hard, smooth surface. The concrete surfaces should be smooth with true, clean arises.  Only very minor surface blemishes should occur and there should be no staining or discoloration from the release agent.

Type D finishes. This finish is obtained by first producing a Type B finish on thoroughly compacted high quality concrete, cast in properly designed forms.  The surface is then improved by carefully removing all fins and other projections, thoroughly washing down and then filling the most noticeable surface blemishes with a cement and fine aggregate paste Every effort should be made to match the color of concrete. Care should be taken. In the choice of any release a gent used. To ensure that the finished concrete surface is not permanently stained or discolored.

Type E finish. This finish is obtained by first producing a Type C finish and then, while the concrete is still green, filling all surface blemishes with a fresh. Specially prepared cement and filing aggregate paste.  Every effort should be made to match the color of the concrete. After the unit has been properly cured. The faces should be rubbed down where necessary, to produce, a smooth and even surface.

Other types of finish. These should be fully specified in each case and should, if possible, be related to samples, which are readily available for comparison. Included under this heading is any finish that requires the course aggregate to be permanently exposed, the use of special

Forms or linings, the use of a different concrete mix nears the surface grinding, bush-hammering or other treatment.

Initial Finishing of Concrete Surface

- The initial finishing must be carried out after the bleeding.

- No spreading of dry cement on the concrete surface is allowed and its.  Recommended to remove the free water carefully by using the sponge pieces.

-It is recommended to use the steel trowel for the finishing surface of the concrete to have a proper surface & without defect. -

Final Finish 0f Concrete Surface

After the stopping of the concrete bleeding and the surface beams dry and before the final setting of concrete, the final finish of concrete can be done (It is recommended to be from 1 - 4 hours).

-Mechanical float is recommended to have a proper concrete surface.

- If none slip surface is required the surface finish of concrete can be brushed to reach the required finish according to the engineer's instructions.

# 4. MASONRY WORKS

# 4.1.General

Generally, the blocks used shall be of local manufacture made with cement and sand in approved vibrated pressure machines. The fine aggregate to be used for blocks shall be clean and sharp. It shall be chemically and structurally stable and shall comply with the Table of Gratings given here under. The cement, fine aggregate and water to be used for blocks shall comply with the requirements given under Concrete Works; and the methods of measuring and mixing the materials shall be the same. The following Mixing Table shall be strictly adhered to in all cases: -

MIXING TABLE

Nominal Cement Sand

Mix Kilos Cu. Meters

360 1.0

TABLE OF. GRADING – PERCENTAGE PASSING

SIZES - % Passing

BS Approximate

Sieve No. Inches Millimeters Sand

- 3 95-100

7 .095 2.4 80-100

14 .47 1.2 60-100

25 .24 .6 30-100

52 .012 .3 5-65 .006 .15 0.15

Note: The above figures represent the limits of percentages (by weight) passing sieves of the sizes mentioned.

The blocks shall be hard, sound, square and clean with sharp well-defined arise sand shall be approved by the Engineer. Hollow blocks, where required, shall be of similar quality and overall size to the said blocks, and shall be of local manufacture made with cement and sand in approved vibrated pressure machines. The design of the cavities and webs shall be submitted to the Engineer for approval before manufacture. The thickness of the membranes or solid portions of hollow blocks shall be not less than 4 cm. each and the combined thickness of the solid portions shall exceed one third of the total thickness in either horizontal direction. Immediately after molding the blocks shall be placed on clean, level, non-absorbent pallets. Blocks shall not be removed from the pallets until inspected and approved by the Engineer. Blocks shall be cured by being kept thoroughly wet by means of water sprinklers or the approved means for a period determined by the Engineer, but in all cases for not less than three days. Blocks must not be left on earth or sand during the curing process. Blocks shall be stacked in honeycomb fashion. Solid stacking will not be permitted.

The average compressive strength of solid blocks shall be not less than 45 kg.lcm2 of gross area at 28 days (average of 12 blocks) such that minimum crushing strength of individual block is not less than 85% of required strength.

The average compressive strength of hollow blocks shall be not less than 35 kg.lcm2 of gross area at 28 days (average of 12 blocks) such that minimum crushing strength of individual block is not less than 85% of required strength.

# 4.2.Mortars

The sand to be used for mortar shall be clean sharp. It shall be chemically and structurally stable and shall comply with the Table of Grading below. The lime to be used mortar shall be imported hydrated lime complying with Class B of British Standard No.890. Where colored -mortars are required these shall be obtained either by the use of colored cement or by addition of pigments complying with British Standard No.1014. The cement and water to be used for mortar shall comply with the requirements given under Concrete Works. The methods of measuring and mixing shall be the same. The following Mixing Table shall be strictly adhere to in all cases: -

| MIXING TABLE |  |  |  |  |
| --- | --- | --- | --- | --- |
| Cement/Sand 1:4 | Cement Kilos 361 | Sand Cubic Meters 100 | Imported Lime (Dry Hydrate) Kilos |  |
| 1:4 Imported Lime with 10% Cement (1:10:2 ½) | 145 | --- Mix | 161 Normal |  |
| ## TABLE OF GRADINGS - PERCENTAGE PASSING |  |  |  |  |
| SIZES |  |  | Sand |  |
| PS | Inches | Approximate | for |  |
| Sieve No. |  | Millimeters | Mortar |  |
| - |  | 5 | 95-100 |  |
| 7 | .095 | 2.4 | 80-100 |  |
| 14 | .047 | 1.2 | 60-100 |  |
| 25 | .024 | .6 | 30-100 |  |
| 52 | .012 | .3 | 5-65 |  |
| 100 | .006 | .15 | 0-15 |  |

Note: The above figures represent the limits of percentages (by weight) passing sieves of      the size mentioned.

The mortar generally shall be cement and sand (1:4) mix. Where plasticiser is added to the mortar the following mixes shall be used: - (a) Building mortar - cement and sand (1:6) and (b (Mortar for pointing - cement and sand (1:3) the palsticiser for jointing-cement and sand (1:3) the palsticiser shall be used strictly in accordance with the manufacturer's instructions. All mortar shall be used before the mitial set has begun. Mortar shall not be re-mixed after the initial set has taken place. The full description given under Section 1 Plaster-work shall apply also to the measuring, mixing, etc. of mortar for Block work.

# 4.3.Construction

All block work shall be set out and built to the dimensions shown on the Drawings. Walls shall be carried up regularly without leaving any part more than one meter lower than another unless the permission of the Engineer is first obtained. In the case of cavity walls both thickness shall be carried up more than about 40 cm. in advance of the other. The courses of block work shall be properly leveled. The perpendicular joints shall be properly lined and quoins, jambs and other angles plumbed at the work proceeds: All walls shall be thoroughly bonded in accordance with the best constructional practice and as directed by the Engineer. Broken blocks shall not be used except where required for bond. All cement and sand blocks shall be soaked with water before being used and the tops of walls left off, and concrete elements in touch shall be wetted before work is recommenced. The faces of walls shall be kept clean and free from mortar droppings and splashes. All blocks shall be properly spread with mortar before being laid and all joints shall be thoroughly flushed up solid through the full thickness of the wall at each course as the work proceeds. For block walls the gauge shall be ten courses to 210 cm. Walls to be left unplastered shall have a fair face consisting of selected blocks pointed with a neat weathered or flush joint as the work proceeds using the same mortar mix as for the jointing. Walls to be plastered shall have the horizontal joints raked out to a depth of 11/2 cm. to form a key. Block work shall be bonded to concrete columns by using non-ferrous metal ties east in concrete of type and dimensions approved by the Engineer.

Cavity walls shall be built to the dimensions shown on the Drawings and the two thickness shall be bonded together with wall ties spaced one meter apart horizontally and approximately 40 cm. apart vertically and staggered. Extra ties shall be provided at reveals, quoins and openings.

The ties shall be of the butterfly twist type of No.10 S.W.G. mild steel wire zinc coated and similar to those described in British Standard No. 1243. The length of the ties shall be approximately 8 cm. less than the total thickness of the wall. The cavity shall be kept clean by lifting screeds or other means approved by the Engineer and shall be left clean at completion. Allowance shall be made for leaving, temporarily; open courses immediately under all structural members built into the walls. These open courses shall be left in suitable positions to permit the structural members to take up their full deflection. The members have been fully loaded and before the completion of the Works.

# 4.4Labors

Arches shall be constructed in purpose-made cement and sand (1:5) mix solid blocks as appropriate to the sizes shown on the Drawings. The Contractor shall provide and erect temporary centering of timber construction and easy, strike and remove on completion. The Contractor shall cut and fit block work around steel work etc., leave or form chases for edges of concrete slabs, Staircases, ends of partitions etc., cut chases for pipes, conduits etc., and make it good. The Contractor shall build all overselling courses, corbels, etc., where shown and build in or out and in ends of sills, steps, lintels, etc., required. Wooden plates and doors and windows frames shall be bedded and exposed edges pointed in mortar and fixing cramps shall be built in. Metal windows shall be bedded in mortar and exposed edges pointed in mastic. Fixing legs shall be built in and channels and frames grouted with mortar. The Contractor shall perform all cutting away and making good for all trades.

Expansion joints as shown on the Drawings or as directed in the Particular Specification shall be constructed generally as either:

a) Open expansion joint with a clean straight cavity of the width directed.

b) Joint filled with an impregnated fiberboard of the thickness directed.

# 4.5.Damp-proof course

Damp-proof course walls shall consist of one layer of tropical quality bitumenised fiber felt damp-proof course complying with Type 5B of British Standard No.743: 1951 weighing not less than 3.25 kg/sq.m (61b/sq.yd). The damp-proof course shall be well lapped at corners and joints and bedded in cement mortar (1:4) mix and pointed both sides. Where shown-on Drawings the Contractor shall similarly provide and build in a vertical damp-proof course at jambs of openings in cavity walls and a horizontal damp-proof course above such openings and to parapet walls.

# 5.METAL AND ALUMINIUM WORKS

# 5.1 Generally

All materials shall be free from scale, rust damage or defects.

All welding, brazing or hot forging shall be carried out by approved processes.

The Engineer shall approve all metalwork before starting painting works.

# 5.2.Aluminum Windows

5.2.1 Performance Requirements

A.	General: Provide aluminum windows engineered, fabricated, and installed to withstand normal thermal movement, wind loading, and impact loading without failure, as demonstrated by testing manufacturer's standard window assemblies representing types, grades, classes, and sizes required for Project according to test methods indicated.

B.	Test Criteria: Testing shall be performed by a qualified independent testing agency based on the following criteria:

1.	Design wind velocity at Project site is 70 mi./h (113 km/h).

2.	Test Procedures: Test window units according to ASTM E 283 for air infiltration, ASTM E 547 for water penetration, and ASTM E 330 for structural performance.

C.	Performance Requirements: Testing shall demonstrate compliance with requirements indicated in AAMA 101 for air infiltration, water penetration, and structural performance for type, grade, and performance class of window units required.

1.	Air-Infiltration Rate for Operating Units: Not more than 0.37 cfm/ft. (2.06 cu. m/h per m) of operable sash joint for an inward test pressure of 1.57 lbf/sq. ft. (75 Pa).

2.	Water Penetration: No water penetration as defined in the test method at an inward test pressure of 15 percent of the design pressure.

3.	Structural Performance: No failure or permanent deflection in excess of 0.4 percent of any member's span after removing the imposed load, for a positive (inward) and negative (outward) test pressure of 30 lbf/sq. ft. (1437 Pa).

5.2.2	Submittals

A.	Product Data for each type of window required, including the following:

1.	Construction details and fabrication methods.

2.	Profiles and dimensions of individual components.

3.	Data on hardware, accessories, and finishes.

4.	Recommendations for maintaining and cleaning exterior surfaces.

B.	Shop Drawings showing fabrication and installation of each type of window required including information not fully detailed in manufacturer's standard Product Data and the following:

1.	Layout and installation details, including anchors.

2.	Elevations at 1/4 inch = 1 foot (1:50) scale and typical window unit elevations at 3/4 inch = 1 foot (1:20) scale.

3.	Full-size section details of typical composite members, including reinforcement and stiffeners.

4.	Hardware, including operators.

5.	Glazing details.

C.	Samples for initial color selection on 12-inch- (300-mm-) long sections of window members. Where finishes involve normal color variations, include Sample sets showing the full range of variations expected.

5.2.3	Quality Assurance

A.	Single-Source Responsibility: Obtain aluminum windows from one source and by a single manufacturer.

B.	he Drawings indicate sizes, profiles, dimensional requirements, and aesthetic effects of aluminum windows and are based on the specific window types and models indicated. Other aluminum window manufacturers whose products have equal performance characteristics may be considered provided deviations in size, profile, and dimensions are minor and do not alter the aesthetic effect.

5.2.4	Project Conditions

A.	Field Measurements: Check window openings by field measurements before fabrication and show recorded measurements on Shop Drawings.

5.2.5 Products

5.2.5.1 Materials

A.	Aluminum Extrusions: Provide alloy and temper recommended by manufacturer for strength, corrosion resistance, and application of required finish, but not less than 22,000-psi (150-MPa) ultimate tensile strength and not less than 0.062 inch (1.6 mm) thick at any location for main frame and sash members.

B.	Fasteners: Provide aluminum, nonmagnetic stainless steel, epoxy adhesive, or other materials warranted by manufacturer to be noncorrosive and compatible with aluminum window members, trim, hardware, anchors, and other components of window units.

1.	Reinforcement: Where fasteners screw anchor into aluminum less than 0.125 inch (3.2 mm) thick, reinforce interior with aluminum or nonmagnetic stainless steel to receive screw threads or provide standard, noncorrosive, pressed-in, splined grommet nuts.

2.	Exposed Fasteners: Except where unavoidable for application of hardware, do not use exposed fasteners. For application of hardware, use fasteners that match finish of member or hardware being fastened, as appropriate.

C.	Anchors, Clips, and Window Accessories: Fabricate anchors, clips, and window accessories of aluminum, nonmagnetic stainless steel, or hot-dip zinc-coated steel or iron complying with requirements of ASTM B 633; provide sufficient strength to withstand design pressure indicated.

D.	Sealant: For sealants required within fabricated window units, provide type recommended by manufacturer for joint size and movement. Sealant shall remain permanently elastic, nonshrinking, and nonmigrating. Comply with Division 7 Section "Joint Sealants" of these Specifications for selection and installation of sealants.

E.	Glass-Fiber-Mesh Insect Screen: 18-by-16 (1.4-by-1.6-mm) or 18-by-14 (1.4-by-1.8-mm) mesh of plastic-coated glass-fiber threads, woven and fused to form a fabric mesh resistant to corrosion, shrinkage, stretch, impact damage, and weather deterioration. Comply with requirements of ASTM D 3656.

5.2.5.2 Hardware

A.	General: Provide manufacturer's standard hardware fabricated from aluminum, stainless steel, or other corrosion-resistant material compatible with aluminum and of sufficient strength to perform the function for which it is intended.

B.	Gear-Type Rotary Operators: Comply with AAMA 901.1 for rotary operators. Comply with ASTM E 405, Method A, when subjected to operating moments and closing torques indicated in AAMA 101.

1.	Provide screw-type system, complete with shafts, brackets, levers, rods, oil-encased gear boxes, and standard fittings and accessories for operation indicated.

C.	Crank-Type Operator: Provide crank-type operator on each gear box shaft, with removable crank. Where necessary, extend crank shaft with universal joints and support brackets to a suitable crank-mounting location not more than 44 inches (1100 mm) above floor, with an oil-encased miter gear box.

5.2.5.3 Accessories

A.	General: Provide manufacturer's standard accessories that comply with indicated standards.

B.	Insect Screens: Provide insect screens for each operable exterior sash or ventilator. Locate screens on inside or outside of window sash or ventilator, depending on window type. Design windows and hardware to accommodate screens in a tight-fitting, removable arrangement, with a minimum of exposed fasteners and latches.

1.	Screen Frames: Fabricate frames of tubular-shaped, extruded- or formed-aluminum members of 0.040-inch- (1-mm-) minimum wall thickness, with mitered or coped joints and concealed mechanical fasteners. Finish frames to match window units.

5.2.5.4 Casement Windows

A.	Window Grade and Class: Comply with requirements of AAMA Grade and Performance Class C-R15. Window units shall successfully pass vertical deflection and hardware load test performance requirements specified in AAMA 101.

B.	Hardware: Provide the following equipment and operating hardware.

1.	Operating Device: Gear-type rotary operator located on jamb at sill.

2.	Hinges: Concealed 4-bar friction hinges with adjustable slide shoe (2 per ventilator).

a.	Provide ventilator operation that provides access for cleaning.

3.	Lock: Lift-type, cam-action lock.

4.	Limit Device: Stay bar with adjustable ehold-open device.

5.2.5.5 Fabrication

A.	General: Fabricate aluminum window units to comply with indicated standards. Include a complete system for assembly of components and anchorage of window units.

1.	Provide units that are re-glazable without dismantling sash or ventilator framing.

2.	Prepare window sash or ventilators for glazing, except where pre-glazing at the factory is indicated.

B.	Thermally Improved Construction: Fabricate window units with an integral, concealed, low-conductance, thermal barrier, located between exterior materials and window members exposed on interior, in a manner that eliminates direct metal-to-metal contact.

C.	Preglazed Fabrication: Preglaze window units at the factory where possible and practical for applications indicated. Comply with glass and glazing requirements of Division 8 Section "Glazing" of these Specifications and AAMA 101.

5.2.5.6 Finishes

A.	Comply with NAAMM "Metal Finishes Manual" for recommendations relative to applying and designating finishes.

B.	Finish designations prefixed by AA conform to the system established by the Aluminum Association for designating aluminum finishes.

C.	Class II, Color Anodic Finish: AA-M12C22A32/A34 (Mechanical Finish: nonspecular as fabricated; Chemical Finish: etched, medium matte; Anodic Coating: Architectural Class II, integrally colored or electrolytically deposited color coating 0.010 mm or thicker).

1.	Color: As selected by Architect from the full range of industry colors and color densities.

5.2.6 Execution

5.2.6.1 Inspection

A.	Inspect openings before installation. Verify that rough or masonry opening is correct and sill plate is level.

1.	Masonry surfaces shall be visibly dry and free of excess mortar, sand, and other construction debris.

5.2.6.2 Installation

A.	Comply with manufacturer's specifications and recommendations for installing window units, hardware, operators, and other components of the Work.

B.	Set window units plumb, level, and true to line, without warp or rack of frames or sash. Provide proper support and anchor securely in place.

1.	Separate aluminum and other corrodible surfaces from sources of corrosion or electrolytic action at points of contact with other materials by complying with requirements specified under "Dissimilar Materials" Paragraph in appendix to AAMA 101.

C.	Set sill members and other members in a bed of sealant or with joint fillers or gaskets, as shown on Shop Drawings, to provide weathertight construction. Refer to Division 7 Section "Joint Sealants" for compounds, fillers, and gaskets to be installed concurrently with window units. Coordinate installation with wall flashing and other components of the Work.

5.2.6.3 Adjusting

A.	Adjust operating sash and hardware to provide a tight fit at contact points and at weather stripping for smooth operation and a weather tight closure.

5.2.6.4 Cleaning

A.	Clean aluminum surfaces promptly after installing windows. Exercise care to avoid damage to protective coatings and finishes. Remove excess glazing and sealant compounds, dirt, and other substances. Lubricate hardware and other moving parts.

B.	Clean glass of preglazed units promptly after installing windows. Comply with requirements of Division 8 Section "Glazing" for cleaning and maintenance.

5.2.6.5 Protection

A.	Provide final protection and maintain conditions, in a manner acceptable to aluminum window manufacturer, that ensure window units are without damage or deterioration at the time of Substantial Completion.

# 5.3.  Aluminum Curtain Walling

The type and dimensions of the aluminum alloy curtain walling shall be as described in the Particular Specification or shown on the Drawings. The curtain walling shall consist of mullions, transoms and head and sill members, to the module shown on the Drawings, fitted together with spigot and socket joint set in non-hardening mastic. The curtain walling shall be of adequate strength to resist the wind pressures, panel loading etc., as shown on the Drawings or in the Particular Specification and shall be securely anchored to the building by means or bolts, channels, etc.; to the approval of the Engineer. Adequate provision shall be made to accommodate thermal movement and suitable weathering devices shall be incorporated.

The system used (solar Semistructural M3 Alumil or equivalent) is a modern curtain wall system with a honeycomb design. The type of construction with isolated panels and isolated columns is designed to withstand both wind and seismic forces associated with the structure. The system’s design also takes into account the expansion co-efficient of aluminum without detriment to the installation and without loss in the elasticity, the durability and weather resistance of the construction.

A wide variety of profiles and complete detailed solutions ensure an impeccable system for all installations. Large columns are also available for constructions that require resistance to high wind loads. The system can be described as a unit and mullion system where the mullions are installed first and pre-assembled panels are then lowered in place behind the mullions.

The panel units may be full-story high, pre-glazed or unglazed or even separate vision glass and spandrel units.

These panels are designed with a small cornice that wraps around the glazing unit to ensure stability without silicone reinforcement and provides the honeycomb design.

The opening panel must designed with the same exterior design as the fixed panels to give uniformity to the overall design.

The system is weather proofed with three gaskets of EPDM and an intelligent draining system which provides condensation control.

All extruded aluminum is powder coated produced by electrostatic powder coating of 80-120 microns thickness, or can be anodized of 20-25 microns thickness.

# 5.4. Sundries

Wrought steel balustrades shall be provided to staircases and balconies as shown on the Drawings. Burglar bars and safety bars shall be provided to windows where shown on the Drawings Cramps for fixing wood door and window frames shall be 20 cm long x 3 cm x 3 mm section and shall have one cud bent and twice drilled for screwing to frame and other end fishtailed for building into walling. Cramps shall be galvanized or dipped in bitumen before fixing Mild steel ladders where required shall be as shown on the Drawings. Metal roller shutters shall be provided to sized shown on the Drawings. Each roller shutter shall be constructed of heavy-gauge metal slats and shall be complete, including channel iron guides, roller box, spindle and counter balance springs and with staple welded to door, hasp set in concrete floor and padlock. The roller shutter -shall- be as stipulated in the Particular Specification.

# 5.5. Custom Steel Door and Frame

5.5.1	Submittals

A.	Product Data: Include construction details, material descriptions, core descriptions, label compliance, sound and fire-resistance ratings, and finishes for each type of door and frame specified.

B.	Shop Drawings: Show fabrication and installation of doors and frames. Include details of each frame type, elevations of door design types, conditions at openings, details of construction, dimensions of profiles and hardware preparation, location and installation requirements of door and frame hardware and reinforcements, and details of joints and connections. Show anchorage and accessories.

C.	Door Schedule: Submit schedule of doors and frames using same reference numbers for details and openings as those on Drawings.

5.5.2 Quality Assurance

A.	Manufacturer Qualifications: A firm experienced in manufacturing custom steel doors and frames similar to those indicated for this Project and with a record of successful in-service performance, as well as sufficient production capacity to produce required units.

B.	Fire-Rated Door Assemblies: Assemblies complying with NFPA 80 that are listed and labeled by a testing and inspecting agency acceptable to authorities having jurisdiction, for fire ratings indicated, based on testing according to NFPA 252.

5.5.3 Delivery, Storage, And Handling

A.	Deliver doors and frames palleted, wrapped, or crated to provide protection during transit and Project site storage. Do not use nonvented plastic.

B.	Inspect doors and frames, on delivery, for damage. Minor damage may be repaired provided refinished items match new work and are approved by Architect; otherwise, remove and replace damaged items as directed.

C.	Store doors and frames under cover at building site. Place units on minimum 4-inch- (100-mm-) high wood blocking. Avoid using nonvented plastic or canvas shelters that could create a humidity chamber. If wrappers on doors become wet, remove cartons immediately. Provide minimum 1/4-inch (6-mm) spaces between stacked doors to permit air circulation.

5.5.4 Products

5.5.4.1 Manufacturers

A.	Available Manufacturers: Subject to compliance with requirements, manufacturers offering doors and frames that may be incorporated into the Work include, but are not limited to, the following:

B.	Manufacturers: Subject to compliance with requirements, provide doors and frames by one of the following:

5.5.4.2 Materials

A.	Hot-Rolled Steel Sheets: ASTM A 569/A 569M, CS (commercial steel), Type B; free of scale, pitting, or surface defects; pickled and oiled.

B.	Cold-Rolled Steel Sheets: ASTM A 366/A 366M, CS (commercial steel), Type B.

C.	Metallic-Coated Steel Sheets: ASTM A 653/A 653M, CS (commercial steel), Type B; with G60 (Z180) zinc (galvanized) or A60 (ZF180) zinc-iron-alloy (galvannealed) coating.

D.	Inserts, Bolts, and Fasteners: Manufacturer's standard units. Where items are to be built into exterior walls, zinc coat according to ASTM A 153/A 153M, Class C or D as applicable.

5.5.4.3 Doors

A.	General: Provide flush-design doors, (2 mm) thick, of seamless hollow construction, unless otherwise indicated. Construct doors with smooth, flush surfaces without visible joints or seams on exposed faces or stile edges.

1.	For single-acting swing doors, bevel both vertical edges 1/8 inch in 2 inches (3 mm in 50 mm).

B.	Nonmetallic Core Construction: Provide the following core construction laminated with waterproof adhesive to both door faces:

1.	Polyurethane Core: Minimum 20-psi (138-kPa) compressive strength and not less than 1.8-lb/cu. ft. (29-kg/cu. m) density foamed-in-place or rigid board polyurethane.

C.	Hardware Reinforcement: Fabricate reinforcing plates from the same material as door to comply with the following:

1.	Hinges and Pivots: 0.167 inch (4.2 mm) thick by 1-1/2 inches (38 mm) wide by 6 inches (150 mm) longer than hinge, secured by not less than 6 spot welds.

2.	Lock Face, Flush Bolts, Closers, and Concealed Holders: 0.093 inch (2.3 mm) thick.

3.	All Other Surface-Mounted Hardware: 0.053 inch (1.3 mm) thick.

D.	Exterior Steel Doors: Fabricate face sheets of doors from two (2mm) thick, stretcher-leveled, metallic-coated steel sheets. Provide weep-hole openings in bottom of doors to permit entrapped moisture to escape. Seal joints in top edges of doors against water penetration.

5.5.4.4	Frames

A.	Fabricate frames of full-welded unit construction, with corners mitered, reinforced, and continuously welded full depth and width of frame. Knockdown frames are not acceptable.

1.	For exterior use, form frames from (3mm-) thick, metallic-coated steel sheets.

2.	For interior use, form frames from cold- or hot-rolled steel sheet of the following thicknesses:

a.	Openings up to and Including 48 Inches (1200 mm) Wide: (3 mm).

b.	Openings More Than 48 Inches (1200 mm) Wide: (3 mm).

B.	Hardware Reinforcement: Fabricate from same material as frame. Minimum thickness of steel reinforcing plates for the following hardware:

1.	Hinges and Pivots: 0.167 inch (4.2 mm) thick by 1-1/2 inches (38 mm) wide by 6 inches (150 mm) longer than hinge, secured by not less than 6 spot welds.

2.	Strikes, Flush Bolts, and Closers: 0.093 inch (2.3 mm).

C.	Head Reinforcement: Where installed in masonry, leave vertical mullions in frames open at top for grouting.

D.	Supports and Anchors: After fabricating, galvanize units to be built into exterior walls according to ASTM A 153/A 153M, Class B.

E.	Jamb Anchors: Weld jamb anchors to frames near hinges and directly opposite on strike jamb as required to secure frames to adjacent construction.

1.	Masonry Construction: Adjustable, flat, corrugated, or perforated T-shaped anchors to suit frame size; formed of same material as frame; not less than 0.053 inch (1.3 mm) thick; with leg not less than 2 inches (50 mm) wide by 10 inches (250 mm) long. Furnish at least the number of anchors per jamb according to the following frame heights:

a.	Three anchors per jamb from 60 to 90 inches (1500 to 2250 mm) in height.

2.	Metal-Stud Partitions: Insert type with notched clip to engage metal stud, welded to back of frames, formed of same material as frame, not less than 0.042 inch (1.0 mm) thick. Provide at least the number of anchors for each jamb according to the following heights:

a.	Four anchors per jamb from 60 to 90 inches (1500 to 2250 mm) in height.

3.	In-Place Concrete or Masonry: Anchor frame jambs with minimum 3/8-inch- (9-mm-) diameter concealed bolts into expansion shields or inserts 6 inches (150 mm) from top and bottom and 26 inches (650 mm) o.c., unless otherwise indicated. Reinforce frames at anchor locations. Except for fire-rated openings, apply removable stop to cover anchor bolts, unless otherwise indicated.

F.	Floor Anchors: Provide floor anchors for each jamb and mullion that extends to floor, formed of same material as frame, 0.067 inch (1.7 mm) thick, as follows:

1.	Monolithic Concrete Slabs: Clip-type anchors, with two holes to receive fasteners, welded to bottom of jambs and mullions.

G.	Head Anchors: Provide 2 head anchors for frames more than 42 inches (1066 mm) wide and mounted in steel-stud walls.

H.	Head Strut Supports: Provide 3/8-by-2-inch (9-by-50-mm) vertical steel struts extending from top of frame at each jamb to supporting construction above, unless frame is anchored to masonry or to other structural support at each jamb. Bend top of struts to provide flush contact for securing to supporting construction above. Provide adjustable wedged or bolted anchorage to frame jamb members.

I.	Rubber Door Silencers: Except on weather-stripped doors, drill stop in strike jamb to receive three silencers on single-door frames and drill head jamb stop to receive two silencers on double-door frames. Install plastic plugs to keep holes clear during construction.

5.5.4.5 Fabrication

A.	Fabricate doors and frames rigid, neat in appearance, and free of defects, warp, or buckle. Accurately form metal to required sizes and profiles. Weld exposed joints continuously; grind, fill, dress, and make smooth, flush, and invisible. Where practical, fit and assemble units in manufacturer's plant. Clearly identify work that cannot be permanently factory assembled before shipment, to assure proper assembly at Project site.

B.	Hardware Preparation: Prepare doors and frames to receive hardware, including cutouts, reinforcement, mortising, drilling, and tapping, according to final hardware schedule and templates provided by hardware contractor. Comply with applicable requirements of ANSI A115 Series specifications for door and frame preparation for hardware.

1.	Reinforce doors and frames to receive surface-applied hardware. Drilling and tapping for surface-applied hardware may be done at Project site.

2.	Locate hardware as indicated or, if not indicated, according to HMMA 831, "Recommended Hardware Locations for Custom Hollow Metal Doors and Frames."

5.5.4.6 Finishes, General

A.	Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for cleaning, treating, priming, and when specified, finishing.

5.5.4.7 Metallic-Coated Steel Finishes

A.	Surface Preparation: Clean surfaces with nonpetroleum solvent so surfaces are free of oil and other contaminants. After cleaning, apply a conversion coating suited to the organic coating to be applied over it. Clean welds, mechanical connections, and abraded areas, and apply galvanizing repair paint specified below to comply with ASTM A 780.

1.	Galvanizing Repair Paint: High-zinc-dust-content paint for regalvanizing welds in steel, complying with SSPC-Paint 20.

B.	Factory Priming for Field-Painted Finish: Apply shop primer specified below immediately after surface preparation and pretreatment. Apply a smooth coat of even consistency to provide a uniform dry film thickness of not less than 0.7 mils (0.02 mm).

1.	Shop Primer: Manufacturer's or fabricator's standard, fast-curing, lead- and chromate-free, primer complying with ANSI A224.1 acceptance criteria; recommended by primer manufacturer for zinc-coated steel; compatible with substrate and field-applied finish paint system indicated; and providing a sound foundation for field-applied topcoats despite prolonged exposure.

      - Steel Sheet Finishes

A.	Surface Preparation: Clean surfaces to comply with SSPC-SP 1, "Solvent Cleaning"; remove dirt, oil, grease, or other contaminants that could impair paint bond. Remove mill scale and rust, if present, from uncoated steel, complying with SSPC-SP 3, "Power Tool Cleaning," or SSPC-SP 6/NACE No. 3, "Commercial Blast Cleaning."

B.	Factory Priming for Field-Painted Finish: Apply shop primer specified below immediately after surface preparation and pretreatment. Apply a smooth coat of even consistency to provide a uniform dry film thickness of not less than 0.7 mils (0.02 mm).

1.	Shop Primer: Manufacturer's or fabricator's standard, fast-curing, corrosion-inhibiting, lead- and chromate-free, universal primer complying with ANSI A224.1 acceptance criteria; compatible with substrate and field-applied finish paint system indicated; and providing a sound foundation for field-applied topcoats despite prolonged exposure.

5.5.5 Execution

5.5.5.1 Installation

A.	General: Install doors and frames according to DHI A115.IG and manufacturer's written instructions.

B.	Frames: Install steel frames for doors and other openings, of size and profile indicated.

1.	Set masonry anchorage devices where required for securing frames to in-place concrete or masonry construction.

a.	Set anchorage devices opposite each anchor location according to details on Shop Drawings and anchorage device manufacturer's written instructions. Leave drilled holes rough, not reamed, and free of dust and debris.

2.	Floor anchors may be set with powder-actuated fasteners instead of masonry anchorage devices and machine screws, if so indicated on Shop Drawings.

3.	Placing Frames: Set frames accurately in position; plumb; align, and brace securely until permanent anchors are set. After wall construction is complete, remove temporary braces and spreaders, leaving surfaces smooth and undamaged.

a.	At existing concrete or masonry construction, set frames and secure in place with machine screws and masonry anchorage devices.

b.	At fire-rated openings, install frames according to NFPA 80.

c.	Field splice only at approved locations. Weld, grind, and finish as required to conceal evidence of splicing on exposed faces.

d.	Remove spreader bars from each frame only after frame is properly set and secured.

C.	Doors: Fit non-fire-rated doors accurately in their respective frames, with the following clearances:

1.	Jambs and Head: 3/32 inch (2 mm).

2.	Meeting Edges, Pairs of Doors: 1/8 inch (3 mm).

3.	Bottom: 3/8 inch (9 mm), if no threshold or carpet.

4.	Bottom: 1/8 inch (3 mm), at threshold or carpet.

D.	Fire-Rated Doors: Install with clearances as specified in NFPA 80.

5.5.5.2 Adjusting And Cleaning

A.	Final Adjustments: Check and readjust operating hardware items just before final inspection. Leave work in complete and proper operating condition. Remove and replace defective work, including doors or frames that are warped, bowed, or otherwise unacceptable.

B.	Prime-Coat Touchup: Immediately after erection, sand smooth any rusted or damaged areas of prime coat and apply touchup of compatible air-drying primer.

# 6. IRONMONGERY

# 6.1.Generally

The Contractor shall provide and fix the ironmongery required by the Particular Specification or shown on the Drawings complete including all necessary screws, bolts, plugs and other fixings.

The use of nails for fixing ironmongery will not be permitted. The Contractor shall hand over all work in a finished state and to the satisfaction of the Engineer

All ironmongery shall be of first quality and shall be obtained from an approved manufacturer. The Contractor will be required to submit for approval samples of all items of ironmongery he proposes to use.

All doors shall be provided with a rubber doorstop plugged and screwed to the floor and all opening sashes of windows shall be provided with friction stays. The size, materials, finishes, type and quality of ironmongery shall be as described in the Particular Specification or shown on the drawings.

6.2 Finish

The finish of the various items of ironmongery shall be as described in the Particular Specification or shown on the drawings.

# 6.3 Fitting and testing

All screws used for fixing ironmongery shall be of the correct type, materials, finish, size and shape to the satisfaction of the Engineer.

The hinges on which doors, windows, fly screen doors, etc. are hung shall be carefully housed or let in to the door, window, fly screen door, etc. and to the frames. All fittings shall be removed before commencing and painting operations and shall be re fixed in place after all painting works are completed and approved by the Engineer.

All ironmongery shall be carefully wrapped and protected until completion of the work and any items or parts, which are damaged or defaced, shall be replaced at the Contractors expense before handing over.

On completion all locks, catches and similar items of ironmongery shall be properly cleaned tested and oiled and all keys be clearly labeled with metal tags approximately 5 cm x 2 cm securely fixed to the keys and handed to the Engineer on approved wooden board.

7. STRUCTURAL STEEL WORKS

7. 1 .  Structural Steelworks

Structural steelworks shall be provided and fixed complete with all plates, cleats, bolts, etc. cut to lengths and sizes and drilled as shown on the drawings. The quality of the steel works generally shall be in accordance with BS 15 (Mild Steel for General Structural Purposes). Steel tubes shall be seamless tubes in accordance with BS 1387 or B.S.1775 All bolts and nuts shall be to International Standard. Black bolts shall be in accordance with BS 916 Bolts shall be of sufficient length to show at least on full thread beyond the nut after tightening. Washers, where used, shall be to BS 3410 with a tolerance of 11/2 mm. (1/16 inch) on the diameter of the hole. The design and detailing of connections and workmanship shall be in accordance with the drawings and BS 49 (The use of Structural Steel in Building).

When bolting to diminishing sections tapered washers shall be used. Riveting shall be carried out in accordance with BS 449 and BS 275 using rivets with snap heads and points and of sufficient length. Surfaces in contact with members to be riveted shall have all burrs removed to ensure perfect contact. Riveting shall be carried out carefully so as to avoid distortion of the riveted members. Welding shall be carried out in accordance with BS 1856 or BS 938 using electrodes as specified in BS 639 or BS 1719. Welders shall be suitably qualified and experienced and, if so required by the Engineer, shall produce evidence of their capability of executing the test welds specified in BS 2645 Part 1. All steelworks fabricated outside the site shall be painted one coat of red lead primer before delivery to the site.

Steel Reinforcement Shop Drawings: Details of fabrication, bending, and placement, prepared according to ACI 315, "Details and Detailing of Concrete Reinforcement." Include material, grade, bar schedules, stirrup spacing, bent bar diagrams, arrangement, and supports of concrete reinforcement. Include special reinforcement required for openings through concrete structures.

8. INSULATIONS

# 8.1 Bitumen Paint

Two coats of hot Bitumen 60/70 must be painted by brush in two perpendicular layers and to be applied for all concrete sections and_ block work _ up to the plinth level as shown in the drawing and according to the Engineer's instructions.

8.2 Installation Of General Building Insulation

A.	Apply insulation units to substrates by method indicated, complying with manufacturer's written instructions. If no specific method is indicated, bond units to substrate with adhesive or use mechanical anchorage to provide permanent placement and support of units.

B.	Seal joints between closed-cell (nonbreathing) insulation units by applying adhesive, mastic, or sealant to edges of each unit to form a tight seal as units are shoved into place. Fill voids in completed installation with adhesive, mastic, or sealant as recommended by insulation manufacturer.

C.	Set vapor-retarder-faced units with vapor retarder to warm side of construction, unless otherwise indicated. Do not obstruct ventilation spaces, except for fire stopping.

1.	Tape joints and ruptures in vapor retarder, and seal each continuous area of insulation to surrounding construction to ensure airtight installation.

D.	Install mineral-fiber blankets in cavities formed by framing members according to the following requirements:

1.	Use blanket widths and lengths that fill cavities formed by framing members. Where more than one length is required to fill cavity, provide lengths that will produce a snug fit between ends.

2.	Place blankets in cavities formed by framing members to produce a friction fit between edges of insulation and adjoining framing members.

E.	Install board insulation on concrete substrates by adhesively attached, spindle-type insulation anchors as follows:

1.	Fasten insulation anchors to concrete substrates with insulation anchor adhesive according to anchor manufacturer's written instructions. Space anchors according to insulation manufacturer's written instructions for insulation type, thickness, and application indicated.

2.	Apply insulation standoffs to each spindle to create cavity width indicated between concrete substrate and insulation.

3.	After adhesive has dried, install board insulation by pressing insulation into position over spindles and securing it tightly in place with insulation-retaining washers, taking care not to compress insulation below indicated thickness.

4.	Where insulation will not be covered by other building materials, apply capped washers to tips of spindles.

8.3 Insulating Materials

A.	General: Provide insulating materials that comply with requirements and with referenced standards.

1.	Preformed Units: Sizes to fit applications indicated; selected from manufacturer's standard thicknesses, widths, and lengths.

B.	Extruded-Polystyrene Board Insulation: Rigid, cellular polystyrene thermal insulation formed from polystyrene base resin by an extrusion process using hydrochlorofluorocarbons as blowing agent to comply with ASTM C 578 for type and with other requirements indicated below:

1.	Type IV, 1.60-lb/cu. ft. (26-kg/cu. m) minimum density, unless otherwise indicated.

2.	Surface-Burning Characteristics: Maximum flame-spread and smoke-developed indices of 75 and 450, respectively.

C.	Molded-Polystyrene Board Insulation: Rigid, cellular polystyrene thermal insulation formed by expansion of polystyrene resin beads or granules in a closed mold to comply with ASTM C 578 for type and with other requirements indicated below:

1.	Type II, 1.35-lb/cu. ft. (22-kg/cu. m) minimum density.

2.	Surface-Burning Characteristics: Maximum flame-spread and smoke-developed indices of 75 and 450, respectively.

D.	Polyisocyanurate Board Insulation: Rigid, cellular polyisocyanurate thermal insulation with core formed by using hydrochlorofluorocarbons as blowing agent and faced on both sides with aluminum foil to comply with referenced standards and with other requirements indicated below:

1.	ASTM Standard: ASTM C 1289, Type I, Class 1 or 2.

2.	Surface-Burning Characteristics: Maximum flame-spread and smoke-developed indices of 75 and 450, respectively, based on tests performed on unfaced core on thicknesses up to 4 inches (101 mm).

3.	Thermal Resistivity: 7.2 deg F x h x sq. ft./Btu x in. at 75 deg F (50 K x m/W at 24 deg C).

E.	Unfaced, Flexible Glass-Fiber Board Insulation: Thermal insulation combining glass fibers with thermosetting resin binders to comply with ASTM C 612, Type IA; or with ASTM C 553, Types I, II, and III; and with other requirements indicated below:

1.	Nominal Density: Not less than 1.5 lb/cu. ft. (24 kg/cu. m) nor more than 1.65 lb/cu. ft. (26 kg/cu. m).

2.	Thermal Resistivity: 4.13 deg F x h x sq. ft./Btu x in. at 75 deg F (28.6 K x m/W at 24 deg C).

3.	Surface-Burning Characteristics: Smoke-developed indices of 25 and 50, respectively.

F.	Foil-Faced, Flexible Glass-Fiber Board Insulation: Thermal insulation combining glass fibers with thermosetting resin binders and faced on one side with foil-scrim-kraft vapor retarder to comply with ASTM C 612, Type IA; or with ASTM C 553, Types I, II, and III; and with other requirements indicated below:

1.	Nominal Density: 1.5 lb/cu. ft. (24 kg/cu. m).

2.	Thermal Resistivity: 4.13 deg F x h x sq. ft./Btu x in. at 75 deg F (28.6 K x m/W at 24 deg C).

3.	Surface-Burning Characteristics: Maximum flame-spread and smoke-developed indices of 25 and 50, respectively.

G.	Unfaced, Glass-Fiber Board Insulation: Thermal insulation combining glass fibers with thermosetting resin binders to comply with ASTM C 612, Type IA and IB; and with other requirements indicated below:

1.	Nominal density of 3 lb/cu. ft. (48 kg/cu. m), thermal resistivity of 4.3 deg F x h x sq. ft./Btu x in. at 75 deg F (29.8 K x m/W at 24 deg C).

2.	Surface-Burning Characteristics: Maximum flame-spread and smoke-developed indices of 25 and 50, respectively.

I.	Foil-Faced, Glass-Fiber Board Insulation: Thermal insulation combining glass fibers with thermosetting resin binders and faced on one side with foil-scrim-kraft or foil-scrim-polyethylene vapor retarder to comply with ASTM C 612, Type IA or Type IA and IB; and with other requirements indicated below:

1.	Nominal density of 3 lb/cu. ft. (48 kg/cu. m), thermal resistivity of 4.3 deg F x h x sq. ft./Btu x in. at 75 deg F (29.8 K x m/W at 24 deg C).

2.	Surface-Burning Characteristics: Maximum flame-spread and smoke-developed indices of 25 and 50, respectively.

N.	Unfaced Mineral-Fiber Blanket Insulation: Thermal insulation combining mineral fibers of type described below with thermosetting resins to comply with ASTM C 665, Type I (blankets without membrane facing).

1.	Mineral-Fiber Type: Fibers manufactured from glass, slag wool, or rock wool.

2.	Surface-Burning Characteristics: Maximum flame-spread and smoke-developed indices of 25 and 50, respectively.

# 8.4Vapor Retarders

A.	Polyethylene Vapor Retarder: ASTM D 4397, 6 mils (0.15 mm) thick, with maximum permeance rating of 0.13 perm (7.5 ng/Pa x s x sq. m).

B.	Vapor-Retarder Tape: Pressure-sensitive tape of type recommended by vapor retarder manufacturer for sealing joints and penetrations in vapor retarder.

# 8.5Auxiliary Insulating Materials

A.	Adhesive for Bonding Insulation: Product with demonstrated capability to bond insulation securely to substrates indicated without damaging insulation and substrates.

# 8.6Insulation Fasteners

A.	Adhesively Attached, Spindle-Type Anchors: Plate welded to projecting spindle; capable of holding insulation, of thickness indicated, securely in position indicated with self-locking washer in place; and complying with the following requirements:

1.	Plate: Perforated galvanized carbon-steel sheet, 0.030 inch (0.762 mm) thick by 2 inches (50 mm) square.

2.	Spindle: Copper-coated low carbon steel, fully annealed, 0.105 inches (2.67 mm) in diameter, length to suit depth of insulation indicated.

B.	Insulation-Retaining Washers: Self-locking washers formed from 0.016-inch- (0.41-mm-) thick galvanized steel sheet, with beveled edge for increased stiffness, sized as required to hold insulation securely in place, but not less than 1-1/2 inches (38 mm) square or in diameter.

1.	Where spindles will be exposed to human contact after installation, protect ends with capped self-locking washers incorporating a spring steel insert to ensure permanent retention of cap.

C.	Insulation Standoff: Spacer fabricated from galvanized mild-steel sheet for fitting over spindle of insulation anchor to maintain air space of dimension indicated between face of insulation and substrate to which anchor is attached.

1.	Air Space: 1 inch (25 mm).

2.	Air Space: 2 inches (50 mm).

3.	Air Space: 3 inches (76 mm).

D.	Anchor Adhesive: Product with demonstrated capability to bond insulation anchors securely to substrates indicated without damaging insulation, fasteners, and substrates.

# 8.7Roofing Insulation

8.7.1 Delivery, Storage, And Handling

A.	Store roofing materials in a dry, well-ventilated, weathertight location to ensure no significant moisture pickup and maintain at a temperature exceeding roofing system manufacturer's written instructions. Store rolls of felt and other sheet materials on end on pallets or other raised surfaces. Do not double-stack rolls.

1.	Handle and store roofing materials and place equipment in a manner to avoid significant or permanent damage to deck or structural supporting members.

- Do not leave unused felts and other sheet materials on the roof overnight or when roofing work is not in progress unless protected from weather and moisture and unless maintained at a temperature exceeding 50 deg F (10 deg C).

C.	Deliver and store liquid materials in their original undamaged containers in a clean, dry, protected location and within the temperature range required by roofing system manufacturer.

D.	Protect roofing insulation materials from physical damage and from deterioration by sunlight, moisture, soiling, and other sources. Store in a dry location. Comply with insulation manufacturer's written instructions for handling, storing, and protecting during installation.

8.7.2 Products

8.7.2.1 Manufacturers

A.	Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

1.	SBS-Modified Bituminous Sheet:

8.7.2.2.  SBS-Modified Bituminous Sheet

A.	SBS-Modified Bituminous Sheet, Smooth Surfaced: SBS-modified asphalt sheet, smooth surfaced, dusted with fine parting agent on both sides; suitable for application method specified; manufacturer's standard thickness and weight; for use and of reinforcing type as follows:

1.	Use: Roof membrane and base flashing.

2.	Reinforcing: Glass-fiber mesh or nonwoven glass-fiber mat.

D.	Physical Properties: Provide SBS-modified bituminous membrane materials with the following properties when tested according to ASTM D 5147:

1.	Thickness: 180 mils (4.5 mm).

2.	Tensile Strength: 185 lbf/in. (32.4 kN/m) at 0 deg F (minus 18 deg C) in each direction.

3.	Elongation at Maximum Load: 4.5 percent minimum at 0 deg F (minus 18 deg C) in each direction.

4.	Tear Strength: 150 lbf (667 N) minimum.

5.	Water Absorption: Less than 0.2 percent mass change.

6.	Low-Temperature Flexibility: Pass at minus 10 deg F (minus 23 deg C).

7.	Compound Stability: Not less than 250 deg F (121 deg C).

8.7.2.3 Auxiliary Membrane Materials

A.	General: Furnish auxiliary materials recommended by roofing system manufacturer for intended use and compatible with SBS-modified bituminous roofing.

1.	Furnish liquid-type auxiliary materials that meet VOC limits of authorities having jurisdiction.

B.	Asphalt Primer: ASTM D 41.

C.	Roofing Asphalt: ASTM D 312, Type III or Type IV, as recommended by modified bituminous membrane manufacturer.

8.7.2.4 Insulation Materials

A.	General: Provide preformed, roofing insulation boards that comply with requirements, selected from manufacturer's standard sizes and of thickness indicated.

1.	Provide preformed, tapered insulation boards where indicated for sloping to drain. Fabricate with the following taper:

a.	As indicated on Drawings.

C.	Faced, Flexible, Glass-Fiber-Board Insulation: Thermal insulation board combining glass fibers with thermosetting resin binders and faced on one side with asphalt-coated fiberglass scrim and kraft paper, complying with ASTM C 726.

D.	Perlite Board Insulation: Rigid, mineral-aggregate thermal insulation board consisting of expanded perlite, cellulosic fibers, binders, and waterproofing agents with top surface seal-coated, complying with ASTM C 728.

8.7.2.5 Insulation Accessories

A.	General: Furnish roofing insulation accessories recommended by insulation manufacturer for intended use and compatible with sheet roofing material.

B.	Protection Mat: Woven or nonwoven polypropylene, polyolefin, or polyester fabric mat, water permeable and resistant to UV degradation, type and weight as recommended by roofing system manufacturer for application.

8.7.2. 6 Aggregate Ballast

A.	Aggregate Ballast: Provide aggregate ballast that will withstand weather exposure without significant deterioration and will not contribute to membrane degradation, of the following type and size:

1.	Aggregate Type: Crushed stone.

2.	Size: ASTM D 448, Size 4, ranging in size from 3/4 to 1-1/2 inches (19 to 38 mm).

8.7.3 Execution

8.7.3.1 Examination

A.	Examine substrates, areas, and conditions under which roofing will be applied, with Installer present, for compliance with requirements.

B.	Verify that roof openings and penetrations are in place and set and braced.

C.	Verify that wood blocking, curbs, and nailers are securely anchored to roof deck at roof penetrations and terminations and match the thicknesses of insulation required.

D.	Do not proceed with installation until after the minimum concrete curing period recommended by roofing system manufacturer.

E.	Do not proceed with installation until unsatisfactory conditions have been corrected.

8.7.3.2 Preparation

A.	Clean substrate of dust, debris, and other substances detrimental to roofing installation according to roofing system manufacturer's written instructions. Remove sharp projections.

B.	Prevent materials from entering and clogging roof drains and conductors and from spilling or migrating onto surfaces of other construction. Remove roof-drain plugs when no work is taking place or when rain is forecast.

8.7.3.3 General Installation Requirements

A.	Install modified bituminous membrane roofing system according to roofing system manufacturer's

B.	Cant Strips: Install and secure preformed 45-degree cant strips at junctures of modified bituminous membrane roofing system with vertical surfaces or angle changes greater than 45 degrees.

C.	Coordinate installing roofing system components so insulation and roofing plies are not exposed to precipitation or left exposed at the end of the workday or when rain is forecast.

1.	Provide cutoffs at end of each day's work to cover exposed ply sheets and insulation with a course of coated felt with joints and edges sealed.

2.	Complete terminations and base flashing and provide temporary seals to prevent water from entering completed sections of roofing system.

3.	Remove and discard temporary seals before beginning work on adjoining roofing.

D.	Asphalt Heating: Heat roofing asphalt and apply within plus or minus 25 deg F (14 deg C) of equiviscous temperature, unless otherwise required by roofing system manufacturer. Do not raise roofing asphalt temperature above the equiviscous temperature range more than one hour before time of application. Do not exceed roofing asphalt manufacturer's recommended temperature limits during roofing asphalt heating. Do not heat roofing asphalt within 25 deg F (14 deg C) of flash point. Discard roofing asphalt maintained at a temperature exceeding 500 deg F (260 deg C) for more than 4 hours. Keep kettle lid closed, unless adding roofing asphalt.

8.7.3.4 Priming Roof Deck

A.	Prime surface of concrete deck with asphalt primer at a rate of 3/4 gal./100 sq. ft. (0.3 L/sq. m) and allow primer to dry.

8.7.3.5 Roof Membrane Installation

A.	General: Install modified bituminous membrane over area to receive roofing, according to manufacturer's written instructions. Extend modified bituminous membrane over and terminate beyond cants.

B.	Two-Ply, Modified Bituminous Membrane: Install 2 plies of modified bituminous membrane, consisting of a base ply and a finish ply, starting at low point of roofing system.

1.	Base- and Finish-Ply Application: Adhere each ply to substrate in a solid mopping of hot roofing asphalt applied at rate required by roofing system manufacturer.

2.	Base- and Finish-Ply Application: Adhere each ply to substrate in cold adhesive, applied within temperature range and at rate required by roofing system manufacturer.

3.	Base- and Finish-Ply Application: Torch apply each ply to substrate.

C.	Laps: Accurately align sheets, without stretching, and maintain uniform side and end laps. Stagger end laps. Completely bond and seal laps, leaving no voids.

1.	Repair tears and voids in laps and lapped seams not completely sealed.

8.7.3.6 Flashing And Stripping Installation

- Install modified bituminous membrane base flashing over cant strips and other sloping and vertical surfaces, at roof edges, and at penetrations through roof, and secure to substrates according to roofing system manufacturer's written instructions and as follows:

1.	Prime substrates with asphalt primer.

2.	Base Flashing Application: Adhere modified bituminous membrane base flashing to substrate in a uniform mopping of hot roofing asphalt, applied to substrate and back of base flashing at rate required by roofing system manufacturer.

B.	Extend base flashing up the wall a minimum of 8 inches (200 mm) above roof membrane and 4 inches (100 mm) onto field of roof membrane.

1.	Seal top termination of base flashing.

8.7.3.7 Protected Membrane Insulation Installation

A.	Loosely lay extruded insulation units over modified bituminous membrane, with long joints of insulation in continuous straight lines with end joints staggered between rows, abutting edges and ends between boards.

1.	Install protection mat over the insulation according to insulation manufacturer's written instructions.

B.	Apply aggregate ballast uniformly over protection mat at rate required by roofing system manufacturer, but not less than the following, carefully spreading to minimize possibility of damage to membrane. Spread ballast as insulation is installed, leaving roof membrane insulated and ballasted at the end of the workday.

1.	Ballast Weight: 10 lb/sq. ft. (50 kg/sq. m), Size 4 aggregate.

8.7.3.8 Field Quality Control

A.	Final Roof Inspection: Arrange for roofing system manufacturer's technical personnel to inspect roofing installation on completion and submit report to Architect.

1.	Notify Architect and Owner 48 hours in advance of the date and time of inspection.

8.7.3.9 PROTECTING AND CLEANING

- Protect modified bituminous membrane roofing from damage and wear during remainder of construction period. When remaining construction will not affect or endanger roofing, inspect roofing for deterioration and damage, describing its nature and extent in a written report, with copies to Architect and Owner.

- Correct deficiencies in or remove modified bituminous roofing that does not comply with requirements, repair substrates, reinstall roofing, and repair base flashings to a condition free of damage and deterioration at the time of Substantial Completion and according to warranty requirements.

# 9. PLASTER WORK AND OTHER WALL AND CEILING FINISHES

# 9.1.MATERIALS

The cement and water used for plastering shall comply with BS specifications. The sand for plastering shall be clean, fine sand and shall be chemically and structurally stable. The sand shall be sieved and graded in accordance with the Table of Grading given below: -

| TABLE OF GRAD ING S-PERCENTAGE PASSING FOR PLASTERING |  |  |  |  |
| --- | --- | --- | --- | --- |
| SIZE |  |  | % PASSING |  |
| BS Sieve No. Inches |  | Approximate Millimeters | Undercoat | Finish Coat |
| 7 | .095 | 2.4 | 95-100 | 100 |
| 14 | .047 | 1.2 | 80-95 | 95-100 |
| 25 | .024 | .6 | 30-55 | 30-85 |
| 52 | .012 | .3 | 5-50 | 5-50 |
| 100 | .006 | .15 | 0-10 | 0-10 |

Note: The above figures represent the limits of percentages (by weight) passing sieves of the sizes mentioned. The gypsum plaster shall be of the hemi-hydrate type with a controlled setting time as Type 6 Clause B of British Standard No. 1191: 1955. The resultant plaster shall be chemically inert when set, be capable of being trowelled to a smooth surface and shall be highly resistant to cracking and crazing. Imported lime shall be of the hydrate type complying with Class B of British Standard No. 890.

9.2.Mixing

The mixing shall be done mechanically and the proportions shall be in accordance with Mixing Table given below: -

| Mixing Table |  |  |  |  |
| --- | --- | --- | --- | --- |
| Nominal Mix | Ratio | Cement Kilos | Sand Cube Meter | Imported Lime(Dry Hydrate) Kilos |
| l:4 cement | -- | 361 | 1.00 | --- |
| 1:1 cement | -- | 442 | 1.00 | --- |
| 1:5 cement with 20% imported Lime | 1:5:1 | 289 | 1.00 | --- |
| 1:4 Imported Lime with 10% Cement | 1:1(1:2%) | 145 | 1:00 | 161 |

With regard to the lime mortars gauged with cement, the addition. Just before use. Of the cement to small quantities of the lime/sand mix shall preferably take place in a mechanical mixing shall continue for such time as will ensure uniform distribution of materials and uniform color and consistency. It is important to note that the quantity of water used shall be carefully controlled Gypsum plaster shall be mixed in a clean pail or other approved vessel The required amount of water shall be placed in the pail and the plaster added gradually and allowed to soak for 5 minutes. It shall then be stirred to a uniform consistency free from lumps and no more material shall be mixed than can be used in half an hour.

9.3.Workmanship

All plastering shall be executed in a neat workman like manner. All races except circular work shall be true and flat and angles shall be straight and level or plumb. Plastering shall be neatly made good up to metal or wood frames and skirting and around pipes or fittings. Angles shall be rounded to 5-mm. radius. Surfaces of undercoats shall be well scratched to provide a key for finishing coats. Screed marks or making good on under-coats shall not show through the finishing coats. Surfaces described as trawled smooth shall be finished with a steel or celluloid trowel to a smooth flat surface free from trowel marks Surfaces described as floated shall be finished with a wood or felt float to a flat surface free from trowel marks. All tools, implements, vessels and surfaces shall at all times be kept scrupulously clean and strict precautions shall be taken to prevent the plaster or other materials from being contaminated by pieces of partially set material which would tend to retard or accelerated the setting time.

# 9.4.Preparation

All surfaces, to be plastered, shall be clean and free from dust, loose mortar and all traces of salts. Where cement plaster is to be applied to surfaces shall first be dashed with a mixture of Portland cement and (1:1) mix to form a key. All surfaces shall be thoroughly sprayed with water and all free water allowed to disappear before plaster is applied. Before plastering is commenced all junctions between differing materials shall be reinforced. This shall apply where walls join columns, where brick walls join block walls and similar situations where cracks are likely to develop and as directed by the Engineer. The reinforcement shall consist of a strip of galvanized wire mesh (10 to 15 mm. hexagonal mesh) 15cms. Wide which shall be plugged, nailed or stapled as required at intervals of not exceeding 50cms. At both edges.

# 9.5.Curing

Plaster shall be cured after the application of each full coat by two days.

# 9.6.Application

After preparation of the surfaces, the undercoat shall be applied to the required thickness between screeds laid, ruled and plumbed as necessary. When nearly set the surface of the undercoat shall be scratched. The undercoat shall be allowed to set hard and shall be curd. Where plastering is applied in one coat or where roughcast is to be applied the scratching should be omitted. The finishing coat shall be applied to the required thickness by means of a laying-on trowel and finished to give the required surface. The sprayed finish shall be applied with an approved machine to give a finish of even texture and thickness. The sprayed finish shall be applied in two separate coat allowing time for drying between coats. Application in one continuous operation to build up a thick layer will not be permitted. The total finished thickness of the two-sprayed coats shall be not less than 3 mm. The sprayed finish shall not be applied until all repairs and making good to the undercoat are completed. Rain-water pipes, fittings and the like shall first be fitted, then removed during the spraying process and refitted and jointed afterwards Any plaster which adheres to other pipes, doors, windows and the like shall be carefully removed before it has set. Curing shall take place after the application of the fourth coat. Plaster should not be allowed to more than 2cm thick. In case it is more wire mish should be used and plaster will be applied in multiple layers.

9.7.Wall Tiling

The tiles for wall tiling shall he true to shape flat and free from flaws. Cracks and crazing and keyed on the reverse side and shall be of a manufacture approved by the Engineer. The tiles shall be specially selected white or colored glazed on face complying with the requirements or British Standard No.l28l The external angles and side and top edges wall tiling shall be formed with rounded edge tiles. At intersections returned rounded edge tiles shall he used. Alternatively where so required by the Particular Specification, the external angles and side and top edges shall be formed with angle beads. Joints shall match the general tiling and at intersections special fittings shall be used. The screed for wall tiling shall be cement and sand (1:3) mix 10 mm thick and the materials, methods of mixing, preparing and applying the screed shall be similar to those described for undercoat. The surface shall be scratched in an approved manner when nearly set to form a key. The surface of the screed shall be well wetted before the tiling is applied. All tiles shall be immersed in clean water for 6 hours or until saturated and all surplus water drained off before bedding. Tiles shall be bedded in cement and sand (1:4) mix 6 mm. thick to a true vertical face with continuous horizontal and vertical joints and pointed in the neat white or colored cement and any surplus which adheres to the face of the tile shall be wiped off with a damp cloth before it sets hard. The joints shall be either close, tight joints or open joints not exceeding 2 mm. wide as required by the Particular Specification. Where tiling abuts against wood or metal frames or other tiling at angles and around pipes etc., it shall be carefully cut and fitted to form a close neat joint. Open irregular joints filled with cement and sand or plaster will not be permitted.

# 9.8.Glass Mosaic:

The mosaic shall be first class local glass mosaic obtained from an approved manufacturer of the colors shown on the Drawings or in the Particular Specification. The individual tiles shall be approximately 25mmx25mmx5mm. thick with an average weight of 12 Kilograms per square Meter. The face of each tile shall be flat and true with opposite edges parallel. The rear edges shall be chamfered. The tiles shall be formed of a homogeneous vitreous paste having a high silica content and The finished tiles shall be opaque and uniform in color throughout their thickness. With the exception of red or yellow tiles, which may be glossy, the face of the tiles should present a malt surface. The mosaic shall be fixed with soluble adhesive to a strong fixing paper in sheets 30cms.x 30cms. The sheets shall be packed in stout cardboard cartons wrapped in waterproof bituminous paper; The cartons shall be contained in a strong wooden case for shipment. To facilitate handling the wooden case shall contain not more than about 3 square Meters. They key coat shall consist of cement and sand (1:5) mix which should be applied four or five days before the mosaic. Application to walls etc., shall generally commence from the bottom working upward by means of throwing the mix vigorously against the surface with a casting trowel and pressing it firmly into joints etc., td ensure adhesion. The surface should be finished plumb and straight and shall be well scratched to form a key. All irregularities of the wall surface shall be well leveled off and the minimum thickness at any point shall be 5 mm. The base coat shall consist of cement and sand (1:5) mix with a proportion of imported hydrated lime of up to 20% by volume added to delay setting. Vertical screeds shall be fixed at edges of surfaces and intermediately as required to permit accurate application of the base coat and shall consist of timber strips 5 mm. to 8mm. thick x 20 mm. wide. The strips shall be coated with mortar as described for base coat, firmly set to the wall and shall be carefully plumbed on face and edge. The key coat shall be well wetted and the base coat shall be applied and carefully leveled between the screeds to give a smooth flat surface which shall be kept moist until the mosaic is fixed. The screeds shall be removed and the base coat leveled up. The bedding coat shall consist of neat white cement and water mixed as previously described for gypsum plaster. The bedding coat shall be applied immediately before the mosaic is fixed to a thickness of 1 mm. Horizontal and vertical reference lines shall be drawn on the bedding coat to ensure accurate fixing of the mosaic. The mosaic sheets shall have their backs coated with a layer of bedding coat mortar, which shall be well trawled in over the whole sheet so that all spaces between tiles are completely filled. The prepared sheets of mosaic shall then be fixed true to level and plumb commencing from the bottom working upwards. Each sheet shall be patted with a steel float especially along the joints between sheets any dropped tiles shall be replaced. The surfaces shall be hammered lightly over a tapered wood block especially where the fixing paper has a dry appearance indicating insufficient penetration of bedding mortar. It is essential that the finished surface be flat and true and that the top edge be leveled. The entire surface shall then be sprayed three or four times with water to soften glue on the fixing paper In cases where the mosaic is exposed to sun or wind the spraying shall be substituted by brushing with a coat of grout similar to the base coat mortar.

When the fixing paper is thoroughly. Wet, it shall be carefully peeled off keeping the hand close to the surface to prevent- dislodging the tiles: The Contractor shall then carry out-any adjustments to tiles which are necessary to render the joints between sheets undetectable.

The surface of the mosaic shall then be sprayed with water and all traces of glue and excess mortar shall be washed off. The surface shall be wiped dry with clean wood shavings. The joints shall then be grouted up using bedding mortar applied by means of a small trowel to ensure that all joints are completely filled for their filled depth. Surplus mortar shall be wiped off with wood shavings. The special edge tiles ("owls beaks") shall then be applied, leveled and grouted. The entire surface shall then be grouted once more and cleaned off with wood shavings. After two to six days at the discretion of the Engineer the surface shall be washed with a 25% solution of hydrochloric acid applied by brush. The surface shall then be sprayed several times with clean water and dried off with clean white rags.

# Carpentry works

    - Description Of Work

- The extent of rough carpentry is shown on the drawings.  The work includes, but is not necessarily limited to, wood grounds, blocking, nailers and the like.

    - Quality Assurance

- Codes and Standards: Comply with the applicable requirements of following codes and standards:

  - APA  - American Plywood Association.

  - AWPB – American Wood Preservers Bureau.

  - U.L – Underwriter’s Laboratories.

    - Submittals

- Submit shop drawings showing full dimensions of each member.  Show details of connections, connectors and other accessories.  Indicate species and stress grade and other variables in required work.

- Wood Treatment Data:  Submit chemical treatment applied and manufacturer’s instructions for proper use of each type of treated material.

- Pressure Treatment:  For each type specified, include certification by treating plant stating chemicals and process used, net amount of salts retained and conformance with applicable standards.

- For water-borne preservatives, include statement that moisture contents of treated material was reduced to maximum of 15% prior to shipment to project site.

- Fire-Retardant Treatment:  Include certification by treating plant that treatment material complies with governing regulations and that treatment will not bleed through finished surfaces.

    - Product Delivery, Storage and Handling

- Keep carpentry materials dry during delivery, storage and handing.  Store lumber and plywood in stacks with provision for air circulation within stacks.  Protect bottom of stacks against contact with damp surfaces.  Protect exposed materials against weather.

- Do not store dressed or treated lumber or plywood out-doors.

    - Job conditions

- Time delivery and installation of carpentry work to avoid delaying other trades whose work is dependent on or affected by the carpentry work and to comply with protection and storage requirements.

- Correlate location framing , furring, nailers, blocking, grounds and similar supports so that attached work will comply with design requirements.

    - Materials

- Timber:

  - General:  Timber for framing, blocking etc., shall be sound, well conditioned, properly seasoned to suite the particular use and free from defects or combination of defects rendering it unsuitable for the purpose intended.  Unless otherwise indicated, timber shall be No.  1 yellow pine or No. 1 fir.

  - Moisture Content:  15% maximum.

- Plywood:

  - concealed Plywood shall be Exterior Type, C-C Grade.

  - Exposed Plywood shall be Exterior Type with medium density overlay on exposed faces.

  - Electrical Panels:  If required for backing panels of electrical and communication equipment, provide Interior type plywood with exterior glue, fire-retardant treated.

- Anchorage and Fastening Materials:  Provide approved type, size, material and finish for each application.

    - Wood Preservative Treatments

- General:  treat lumber and plywood, where required or indicated as “Treated”, to comply with the applicable requirements of the American Wood Preservers Bureau (AWPB), available form AWPI.

- Pressure treat the following items with waterborne preservatives for above-ground use, complying with AWPB LP-2:

  - Wood cants, nailers, blocking, stripping and similar members in connection with roofing, flashing, vapour barriers and waterproofing.

  - Wood blocking, furring, stripping and similar concealed members in contact with masonry or concrete.

- Kiln-dry wood to a maximum moisture content of 15% after treatment with water-borne preservatives.

- Pressure treat wood members placed in the ground with below-round water-borne preservatives, complying with AWPB LP-22.

    - Fire Retardant Treated Wood

- Where fire-retardant treated plywood is specified, comply with AWPB standards for pressure impregnation with fire-retardant chemicals to achieve a flame spread rating of not more than 25 when tested in accordance with UL Test 723, ASTME 84, or National Fire Protection Association (NFPA) Test 355.

  - Where transparent or paint finish is shown or scheduled for treated wood, use a fire-retardant treatment which will not bled through or adversely affect bond or finish.

- Complete fabrication prior to treatment, wherever possible, to minimise cutting and jointing after treatment.  Coat surfaces cut after treatment with a heavy brush coat of the same fire-retardant chemical.

- Kiln-dry lumber and plywood to a maximum content of 15% after treatment.

- Inspect each piece of plywood after drying; do not use twisted, warped, bowed or otherwise damaged or defective pieces.

- Provide UL label or other equivalent on each piece of fire- retardant treated wood.

    - Inspection

- The Contractor shall examine the substrates and the conditions under which rough carpentry work shall be carried out and correct any unsatisfactory conditions.  Do not proceed with the work until unsatisfactory conditions have been corrected in a manner acceptable to the Engineer.

    - Installation

- General:  Discard units of material which are unsound, warped, bowed, twisted, improperly treated, not adequately seasoned or too small to fabricate the work with a minimum of joints or the optimum jointing arrangement.

- Shop Drawings:  Comply with details shown on approved shop drawings.  Provide lumber and plywood of dimensions not less than those shown.

- Fit carpentry work to other work.  Scribe and cope as required for accurate fit.

- Set carpentry work accurately to required levels and lines with members plumb and true.

- Securely attach carpentry work to substrates by anchoring and fastening as shown and as required by recognized standards.

  - Provide washers under bolt heads and nuts in contacts with wood.

  - Nail plywood to comply with recommendations of the American Plywood Association.

  - Countersink nail heads on exposed carpentry work and fill holes.

- Fasteners:

  - Use common wire nails, except as otherwise shown or specified herein.  Use finishing nails for exposed work.  Do not wax or lubricate fasteners that depend on friction for holding power.  Select fasteners of size that will not penetrate members where opposite side will be exposed to view or will receive finish materials.  Make tight connections between members.

  - Install fasteners without splitting of wood, predrill as required.  Do not drive threaded friction type fasteners; turn into place.  Tighten bolts and lag screws at installation and retighten as required for tight connections prior to closing or at completion of work.

    - Wood Grounds, Nailers, Framing and Blocking:

1. Provide wherever shown and where required for screeding or attachment of other work.  Form to shapes as shown and cut as required for true line and level of work to be attached or screeded.

2.Coordinate location with other work; refer to shop drawings of such work, if any.

3.Attach to substrates securely with anchor bolts or other attachment devices as shown and as required to support applied loading.  Countersink bolts and nuts flush with surfaces, unless otherwise indicated.  Build into masonry as work progresses, cutting to fit masonry unit size involved.  Anchor to formwork before concrete placemen.

4.Provide grounds of  dressed, dey-bevelled lumber not less than 38mm wide and the thickness required to bring face of ground to exact thickness of finish material involved.  Remove temporary grounds when no longer required.  Where indicted as permanent grounds, provide treated lumber.

10. PAINTING AND DECORATING

10.1.Generally

Every possible precaution shall be taken to keep down dust before and during painting processes. No paint shall be applied to surfaces structurally or superficially damp and all surfaces must be ascertained to be free from condensation, efflorescence, etc. before the application of each coat. Primed or undercoated woodwork and metal work should not be left in an exposed or unsuitable situation for an undue period before completing the painting process. No exterior or exposed painting shall be carried out under adverse weather conditions such as rain, extreme humidity, dust storms, etc. Metal fittings such as ironmonger etc. not required to be painted shall first be fitted and then removed before the preparatory, processes arc commenced. When all painting is completed the fittings shall be cleaned and re fixed in position. The Contractor will be required to repaint at his own expense any work on which the paint is found to be incorrectly' applied. The Contractor shall be responsible for protecting from damage the paint work and all other work during and after painting operations including the provision of all necessary dust heats, covers, etc. Brushes, pails, kettles etc. used in carrying out the work shall be clean and free from foreign matter. They shall be thoroughly cleaned before being used for different types or classes of material.

# 10.2.Materials

The decorating materials shall be obtained from approved manufacturers and shall be supplied in the manufacturers' sealed and branded containers. All materials must be thoroughly stirred before use. Details of mixing and application shall be in accordance with the specifications of the manufacturers concerned and to the approval of the Engineer. The mixing of paints etc., of different brands before or during application will not be permitted. No dilution of painting materials shall be allowed except strictly as detailed by the manufacturers and as approved by the Engineer. Fillers shall be "Polyfilla"; or other equal and approved. Thinners shall be approved turpentine or white spirit. Priming paints shall be:

For woodwork: Leadless gray priming paint in accordance with British Standard No.2522. Alternatively wood work of hard, non-absorbent timber. Resinous timber of prominent grain shall be primed with one coat of aluminum sealer equal to "A 519-3648" .

For steelwork: Red oxide priming paint in accordance with British Standard No.2524. For galvanized, zinc or aluminum alloys surface. Gray zinc chromate priming paint equal to “A500-388”.

Knotting shall be in accordance with British Standard No.1336. Stopping shall be hard stopping composed of paste white lead, gold size whiting.

Undercoating shall be:

Zinc oxide based undercoating paint.

White lead based undercoating paint in accordance with British Standard No.2525 Colors shall approximate to the finishing paint.

Synthetic alkyd based undercoating paint

Finishing paints shall be:

- Zinc oxide based oil paint in accordance with British Standard Nos. 277 and 278.

- White lead based oil gloss finishing paint in accordance with British Standards Nos. 2526 and 2527

- Synthetic alkyd based finishing paint

Petrifying liquid shall be used undiluted as supplied by' the manufacturer. A small quantity of water paint of the finishing color may be mixed with the petrify-mg liquid. Water paint shall be an approved brand of washable oil-bound water paint complying with British Standard No. 1053 Type A. Thinning shall be done with petrifying liquid or fresh water only. Emulsion paint shall be of the Polyvinyl Ac9tate (P.V.A.) type obtained from an approved manufacturer. The precise specification shall comply with the manufacturer's normal practice. In all cases thinning  -shall be done with thinners supplied by the manufacturer or fresh water only. Stain for woodwork shall be an approved brand of oil stain complying with British Standard No. 1215. Varnish for woodwork shall be an approved brand of exterior oil varnish complying with British Standard No.257, No.2 Pale.

PREPARATION PROCESS

# 10.3.Internal Plaster, Fair faced Concrete and Block work

Surfaces shall be allowed to dry out completely and cracks shall be cut out and made good with suitable hard plaster or cement/sand mix as appropriate, such repaired portions shall be allowed to dry out. No painting shall be carried out on plastering less than five weeks old. Efflorescence shall be completely removed by rubbing down with dry coarse cloths followed by wiping down with damp cloths and allowed to dry. All surfaces shall be rubbed down with fine glass paper and brushed free of dust before applying any form of decoration. Surfaces which are to receive water paint shall be treated with one coat of petrifying liquid applied by brush and allowed to dry for at least twenty four hours before the application of water paint. A period of twenty four hours or longer if necessary, shall be allowed between subsequent coats. Fair faced concrete and/or cement and sand plastered surfaces, which are to receive oil paint shall be given one thin coat of oil putty and allowed to dry for at least two days. The surfaces shall then be rubbed down with fine glass paper and given a second thin coat of oil putty when completely set shall be rubbed down again with fine glass paper before applying the priming coat of oil paint. All surfaces, which are to receive oil paint, shall be treated with one coat of alkali resisting priming applied by brush and allowed to completely harden.

# 10.4.Ceiling Boards etc.

Soft Boards, where used externally or under humid conditions, will receive one coat of priming paint and one coat of undercoat on back, face and edges. Soft Boards, where used internally, will receive one coat of priming paint and one coat of emulsion paint on back, face and edges. Hardboard. Composite panels will be treated in the same way as soft boards under humid conditions. Acoustic will be treated on the face in the same way as plaster Boards but the paint may be applied by spray; the backs and edges should not be treated. Asbestos. If surfaces are to receive oil paint later one coat of priming paint should be applied. If surfaces are to receive water paint or emulsion paint no priming paint will be necessary.

# 10.5.Steelworks including Windows, Louvers, etc. Internally and externally.

If delivered galvanized, the surfaces shall be cleaned to remove grease and dirt before priming. Where rusting has occurred through damage to the galvanizing, such rust shall be removed by wire brushing back to clean metal and the galvanizing made good with a rust-inhibiting agent. The surface shall then be treated with one coat of mordant solution and one coat of zinc chromate priming, paint. If delivered primed. The surfaces shall be examined to ascertain that the priming paint is hard, firmly adhering and in good condition. If not satisfactory, the priming paint shall be removed and the surfaces cleaned to remove grease and re primed. If the condition shall be cleaned to remove grease and dirt. Minor damage to the priming paint being made with red oxide priming paint after removal of rust. If delivered unprimed and not galvanized, the surfaces shall be cleaned to remove grease and dirt, and wire brushed and scraped to remove all rust and scale before applying a red oxide priming paint. Priming paint shall be brushed well into the surface and shall be allowed to dry and harden thoroughly before the application of subsequent coats. Items of steelworks such as frames to roller shutters, covers to expansion joints, etc., which are to be built into walls first be primed.

# 10.6.Exposed Service Pipes

Copper, aluminum and brass pipe work shall have the surfaces slightly a braided with glass paper and white spirit or similar solvent and wiped clean. No priming paint will be necessary, the surfaces being finished in two coats of glass paint. Steel pipes will be treated as for steelworks with the exception that galvanized pipes are to be treated with a zinc chromate priming paint. Coated soil pipes shall be wiped clean and treated with two coats of knotting followed by priming paint as described above.

# 10.7. Woodwork required to be painted

Surfaces shall be cleaned to remove grease and dirt. The surface of teak shall be cleaned with white spirit to remove free oil. The preparation process shall then be. Knot. All knots shall be treated with shellac knotting Prime. One coat of primer shall be thoroughly applied by brush to all surfaces and when dry a further coat to be applied to end-grain surfaces stop. When priming paint is hard, all cracks, holes open joints etc. shall be made good with hard stopping and all open grain surfaces filled smooth with linseed oil putty or an approved filler and rubbed down with Fine glass paper.

No joinery shall be primed until the Engineer has approved it. Priming shall be carried out on the Site and not in the factory. Items of carpentry work which are to be built into walls etc. shall be first treated by twice coating with creosote or other approved preservative.

# 10.8. Woodwork required to be stained and varnished.

Surfaces shall be cleaned to remove grease and dirt. The wood shall then be stopped, filled and robbed down. In the case of teak free oil shall be removed by cleaning with white spirit.

# 10.9 FINISHING PROGRESS

10.9.1 	Internal Plaster

Where emulsion paint is specified two coats shall be applied by brush in addition to any priming paint. Where water paint is specified two coats shall be applied by brush in addition to the petrifying liquid. The water paint shall be thinned to the consistency of thick mream. Where oil paint is specified this shall be two or three coat work as detailed in the Particular Specification, applied by roller or brush, but not by spray, to produce hard gloss, oil gloss, eggshell or flat finish as required. The finishing coat of paint to walls and ceilings shall be applied after the completion testing of the electrical installation. Any paint splashes on electrical fittings shall be carefully cleaned off.

10.9.2 Ceiling Boards Etc.

Both acoustic and plain ceiling boards will be treated as for plaster, but the paint may be applied by spray. Water paint or emulsion paint shall be applied by brush to the specification of the manufacturers. Where a ceiling board is likely to be exposed to extreme humidity, i.e. kitchen and external corridors and covered ways, an oil paint shall be used on the face after fixing.

10.9.3 Unflustered Concrete or Block work

As for plastered surfaces. Externally a cement type paint may be used, and shall be applied keeping a constantly wet edge, in strict accordance with the manufacturer's instructions.

10.9.4 Steelworks and Exposed Service Pipes

Internally, apply one coat gloss paint over two undercoats. Non-ferrous pipes shall be finished in two coats of gloss Externally, apply two coats gloss paint over one undercoat.

10.9.5 Woodwork required to be Stained and Varnished

The woodwork, internally and externally, shall be stained as directed on Site, rubbed down, brushed _off and treated with two coats of varnish. If the varnish is found to be tacky after two or three d4ys it shall be washed off with turpentine and re-executed from a new supply of varnish at the Contractor's own expense.

10.9.6. External Rendering

Painting of external rendering will be avoided, the colors generally being obtained in the rendering. A tallow lime wash shall be used where necessary.

Note: All precautions should be done to avoid any damages to already executed works during painting process.

11.PAVIOR (INCLUDING MARBLE AND TERRAZZO WORKER)

# 11.1. Materials

Portland cement, fine aggregate and water shall be as previously specified in section 3, concrete works.

The colour pigments shall be of an approved manufacture, lime-proof and non-fading and complying with British Standard No. 1014: 1942.

The marble chipping shall be of an approved quality in irregular pieces varying for 0.047 to 3/8 in size defending on the effect required. The pieces should preferably be roughly cubical in shape and flaky shaped pieces shall not be used.

The granite chipping shall be of an approved quality graded from ½ down with not more than 5% fine material passing a No. 100 sieve.

Marble and granite aggregates shall comply generally with table and granite aggregates shall comply generally with table of gradings. In connection with marble aggregates the percentages are approximate only. The actual gradings should be selected to produce the surface effects required.

| Table of grading – percentage passing |  |  |  |  |
| --- | --- | --- | --- | --- |
| Sizes |  |  |  |  |
| B.S. Sieve No. |  |  |  |  |
| - | ½ | 13 | 100 | - |
| - | 3/8 | 10 | 59-100 | 59-100 |
| - | 3/16 | 5 | 30-60 | 25-60 |
| 7 | 0.095 |  | 20-50 | 5-30 |
| 14 | 0.047 | 1.2 | 15-40 | 0-10 |
| 25 | 2.4 | 0.6 | 10-30 | - |
| 52 | 0.012 | 0.15 | 5-50 | - |
| 100 | 0.006 | 0.3 | 0-5 | - |

Note: The above figures represent the limits of percentages (by weight) passing sieves of the sizes mentioned.

# 11.2 Mixing

Materials for in-situ paving and locally manufactured tiles shall be measured separately in approved gauge boxes on a clean, dry, level surface.

Materials shall be mixed either by hand or machine as previously specified in Section 3, concrete works.

# 11.3 Proportions

The following mixing table shall be strictly adhered to in all castrations will be permitted only when demanded by the particular Specification for individual works or prior written consent of the Engineer.

| Mixing table |  |  |
| --- | --- | --- |
| Nominal mix | Cement Kilos | Fine Aggregates Cu.M. |
| 1:1 | 1442 | 1.00 |
| 1:2 | 721 | 1.00 |
| 1:2 ½ | 577 | 1.00 |
| 1:3 | 476 | 1.00 |
| 1:4 | 361 | 1.00 |
| 1:5 | 289 | 1.00 |

# 11.4 Granolithic Paving

These shall consist of a (1:2 ½ ) mix-one part Portland cement to two and half parts of granite aggregate mixed with sufficient water to give a suitable plasticity for laying. Generally the paving shall be laid immediately following the concrete sub-base. If these paving are laid on a matured concrete sub-see the concrete shall first well cleaned wetted and brushed with a Portland cement grant.

To produce a wearing surface the granolithic mixture shall be tamped in with a wood float and trawled twice with a steel trowel to produce a smooth finish.

The paving shall be laid in alternate bays not exceeding 9 square meters in area and the bays shall be separated by expansion strips of brass or other approved material.

Covering them with Hussein wet for seven days shall cure granolithic paving.

# 11.5 Cement and sand paving

These shall consist of a (1:3) mix-one part of Portland cement to three parts of sand mixed with sufficient water to give a suitable plasticity for laying. Generally the paving shall be laid immediately following the concrete sub-base. If laid on a matured concrete sub-base the same precautions should be taken as described for granolithic paving above.

The paving shall be laid in bays as prescribed above for granolithic paving.

Cement and sand paving intended as a wearing surface shall be trawled twice with a steel trowel to produce a smooth finish. In addition two coats of sodium silicate solution shall be brushed on.

Cement- sand paving shall becrued as described above for granolithic paving.

# 11.6 Cement and sand tiles

These shall be formed with a (1:2) mix of white or colored cement, or in white cement with a colour pigment added, and sand applied as a facing not less than 7 ½ mm thick to a Portland cement and sand (1:5) mix backing. The tiles shall be cast in heavy metal moulds under pressure to the proportions and sizes shown in the following table.

| Grinding of granite and marble chipping |  |  |  |  |
| --- | --- | --- | --- | --- |
| sizes |  | Percentage passing by Weight |  |  |
| B.S. Sieve No. | Approximate Millimeters | ## Inches | Granite Chipping | Marble Chipping |
| - | 13 | ½ | 100 | - |
| - | 10 | 3/8 | 95-100 | 95-100 |
| - | 5 | 3/16 | 30-60 | 25-60 |
| 7 | 2.4 | 0.095 | 20-50 | 5-30 |
| 14 | 1.2 | 0.47 | 15-40 | 0-10 |
| 25 | 0.6 | 0.24 | 10-30 | - |
| 52 | 0.3 | 0.12 | 5-50 | - |
| 100 | 0.15 | 0.006 | 0-5 | - |

It is essential that closer grading limits be selected for the marble chipping if a consistent and uniform surface texture is desired.

Coloured cement and sand skirting to match tiles, 10cm or 20cm with chamfered top edges shall be produced in the same way as the tiles using the same mixes.

All cement and sand tiles shall be cured by totally immersing them, after the initial set has taken place, in a tank of clean water for at least 24 hours.

Cement and sand tiles shall be laid and bedded direct on to a concrete sub-floor on a cement and sand 1:4 mix screed. This screed shall be laid and bedded direct on to a concrete sub-floor on a cement and sand 1:4 mix screed. This screed shall be 2 ½ cm thick in the castoff 2 ½ cm tiles and 3cm thick in the case of 2cm tiles. The total thickness of cement and sand screed and tiles shall not exceed 5 cm. All tiles shall be laid with square joints.

All cement and sand tiles shall be cured by totally immersing them after the initial set has taken place I a tank of clean water for at least 24 hours.

Cement and sand tiles shall be laid and bedded direct on to a concrete sub-floor on a cement and sand 1:4 mix screed. This screed shall be 2 ½ cm thick in the case of 2 ½ cm tiles and 3 cm thick in the case of 2cm tiles. The total thickness of cement and sand screed and tiles shall not exceed 5cm. All tiles shall be laid with square joints.

All tiling shall be grouted up on completion, care being taken to fill all joints completely. The grout shall consist of net cement of a color to match the tiling. Any surplus grout shall be cleaned off the face of tiling and surrounding surfaces immediately and all tiling shall be carefully cleaned off.

# 11.7 Terrazzo Tiles

These shall be formed with a (1:2 ½) mix of white or colored cement or white cement with a colour pigment added and granular marble chipping applied as a facing not less than 5mm thick to a Portland cement and sand 1:5 mix backing.

The tiles shall be cast in heavy metal moulds under pressure to the proportions and sizes shown in the following table.

| Terrazzo tile dimensions |  |  |
| --- | --- | --- |
| Size (cm) | Size tolerances(mm) | Total Thickness(mm) |
| 20x20 | 0.5 | 20 |
| 25x25 | 0.5 | 25 |
| 30x30 | 1.0 | 25 |
| 40x40 | 1.0 | 30 |

Tiles shall be cured as for cement and sand tiles and then ground, filled and polished before distribution to Site. Grinding shall be done wet by means of a No. 80 carborundum stone. Filling shall be carried out with neat cement grout of the same colour as the facing mix and this shall be worked into the surface with a wooden shaper to fill all voids and air holes. Surplus grout shall be removed with a dry cloth. After a minimum period of 24 hours polishing shall be carried out wet by means of a No. 140 carborundum stone.

Terrazzo skirting 10 cm or 20 cm high with chamfered top edge shall be produced in the same way as for tiles using the same mixes.

Terrazzo tiles shall be laid and bedded direct on to a concrete sub-floor on a cement and sand 91:4) mix screed. This screed shall be 2 ½cm thick in the case of 2 ½ tiles and 3cm thick in the case of 2cm tiles. The total thickness of the cement and sand screed and tiles shall not exceed 5cm. All tiles are laid with square joints.

All tilling shall be grouted up on completion, care binge taken to fill all joints completely. The grout shall consist of neat cement of a colour to match the tilling. Any surplus surfaces immediately and all tilling shall be carefully cleaned off.

All terrazzo surfaces shall be polished on completion. Large areas such as floors shall be wet polished by means of approved machines using No. 140 carborundum wheel. Any surface too small for convenient machine polishing may be polished by hand using a No. 140 carborundum stone and water. Care must be taken during any polishing operation not to damage any angles or arises.

Terrazzo covering to items such as cills, treads and risers to steps, skirting etc., shall generally be applied in accordance with the foregoing specification except that the thickness of the facing shall be at least 10mm thick.

# 11.8 Marble Paving

Marble paving shall generally be 2-3 cm thick the size, type and pattern that be as stated in the particular specification, BOQ and/or shown on the drawings.

The marble slabs shall be fixed solid on a bed of cement and sand 1:4 mix 3cm thick tight joints grouted in lime putty. Protective slurry of putty at least 3mm thick shall be applied to the marble paving and subsequently cleaned off.

Treads to stairs shall be 2cm thick fixed solid on a bed of cement and sand 1:4 mix 3cm thick Risers to stairs shall be 2cm thick fixed solid on a backing of cement and sand 1:4 mix 3cm thick. Window cills shall be 3cm thick bedded hello on plaster slabs. Skirting shall be 1cm thick in lengths equal to the tile length, fixed solid on a backing of cemented sand 1:4 mix 2cm thick. Joints in skirting shall be arranged to coincide with joints in adjacent paving. Rounded arises, noising and moldings shall be adequately protected by means of timber casing or lime putty ceilings. Treads, risers, skirting and windows cills shall be grouted and protected in a manner similar to paving.

The exposed faces and adges of all marble shall be polished smooth and be free from scratches or other defects.

# 11.9 Marble linings

Marble linings to walls, columns and the like shall generally be 2cm thick and the size, type and pattern shall be as stated in the particular specification, BOQ and/or as shown on the drawings. The marble slabs shall be cut square/rectangular and true and shall be uniform in shape and thickness. Patterns and moldings shall be accurately formed in accordance with the Drawings.

The marble slabs shall be fixed with copper cramps and books and plaster rabs leaving an air space of 12mm behind the slabs to prevent transfer of soluble salts from the backing materials. The cramps shall be 2 1/2cm x 5mm x 10mm girth one end and turned down and grouted into mortise in marble and the other and built into wall set 45cm apart in each bed. Mortises shall be accurately and carefully cut and all joints shall be thoroughly grouted.

Exposed edges and molding shall be protected by means of timber casings or lime putty coatings.

The exposed edges and faces of all marble shall be polished smooth and shall be free from scratches or other defects.

# 11.10 Generally

All paving shall be protected from damage during subsequent operations and shall be well washed and thoroughly cleaned before handing over.

# 11.11 Tiles Testing

All paving shall be protected from damage during subsequent operations and shall be well washed and thoroughly cleaned before handing over.

The tiles must be tested according to the international standards and as follow: -

Water Absorption: Absorption should not be more than 8% by weight for each sample.

Transverse Strength: It should not be less than 3 N/mm2 for each sample.

Wear Resistance	: Rate of wear resistance should not be more 2mm on average for 3 samples of each batch.  However each sample should not have wear resistance over 2.5 mm.

# 11.12 Tiles and Cladding

All the tiling & cladding works will be executed according to the drawings and engineers instructions and will be tested to control the quality of the materials as mentioned in the general specifications. Unless otherwise said in the BOQ and drawings, the tiling will be:

- Terrazzo tiles (local production):

- Terrazzo (marble chips) floor tiles size 25x25x2.5cm.

- Terrazzo (marble chips) skirting 1x7cm.

- Marble Works:

- Local marble (Yatta) 3cm thick will be used for doors entrances WCs, and main entrances.

- Local marble (Yatta) copings 3cm thick will be used for staircases and roof parapets.

- Perlato marble 30x60x3cm tiles will be used for flooring.

- Colored marble (preganza 2.0cm thick with sizes as requested by the engineer).

- Windows sills will be local marble 3 cm thick (from Yatta).

- The kitchen cabinets :

- Local marble (3cm thick from Yatta) will be used for dividers, shelves, floor and back of the kitchen cabinets and the work top will be from Tiger Eye marble from Italy, the cupboard leaves will be of 12mm thick ordinary plywood covered with colored Formica 1mm thick.

- West Bank stone: -

- West Bank stone of 5.0cm thick from Jamaeen-First Choice will be used as shown in the drawings and the engineer’s instructions.

# Porcelain Wall tiles

The porcelain shall be first class obtained from approved manufacturer of the colors and sizes shown on the drawings or in the particular specifications.

The tiles should conform to the international specifications regarding:  water absorption, flexion resistance, hardness, color resistance to light, resistance to chemicals,…etc.

The tiles should be layed according to the manufacturers instructions, and according to the following guide lines:-

- The wall surface is to be clean and free of steel wires or any other materials.  A prime coat of sand cement mixture (450 kg cement / m3) is to be applied and treated by spraying with water for three days at least.

- A base coat of plastering with average thickness of 2cm is to be applied after the full treatment of the prime coat. The base coat mixture consists of at least 300 kg/m3 of cement. A proportion of imported hydrated lime of up to 20% by volume may be added to delay setting.  The surface should be finished plumb and straight and shall be treated by spraying with water for 5 days at least.

- The porcilane tiles are to be laid upon the completely treated base coat using the special materials recommended by the manufacturer and in full compliance with the technical instructions of the manufactures.

# 12. GLAZING

12.1 Materials

Clear glass shall be flat-drawn clear sheet glass complying with British standard No. 952 section 1, ref: “ Ordinary Glazing Quality” of the substances shown below:

| Nominal substance | Limits of thickness | Possible Variation in weight |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Ounces | Millimeters | Per foot super per meter super |  |  |  |
|  |  | Min | Max | Min | Max |
|  |  | Oz. | Oz. | Kg. | Kg. |
| 24 | 2.75 - 3.05 | 22.50 | 25.25 | 6.86 | 7.70 |
| 26 | 3.10 - 3.50 | 26.00 | 28.75 | 7.93 | 8.77 |
| 32 | 3.90 – 4.30 | 31.75 | 35.25 | 9.68 | 10.75 |

# 12.2 Plate glass

Plate glass shall be cast, rolled or drown glass ground and polished on both surfaces complying with British standard no. 952 section 1 ref: ‘Glazing for glazing quality’ of the substance shown below

| Nominal substance inches | Limits of thickness |  | Possible variation in weight per foot super per meter |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Inches – millimeters |  | Min |  | Max |  | Min | Max |
|  |  |  | Ib. | Oz. | Ib. | Oz. | Kg | Kg |
| 3/16 | 10/64-14/64 | 3.97-5.56 | 2 | 0 | 2 | 14 | 9.76 | 14.03 |
| ¼ | 14/64-20/64 | 5.56-7.94 | 2 | 13 | 4 | 1 | 13.73 | 19.83 |
| 3/8 | 23/64-27/64 | 9.13-10.72 | 4 | 10 | 5 | 8 | 22.57 | 26.84 |
| ½ | 30/64-34/64 | 11.91-13.49 | 6 | 1 | 6 | 15 | 29.59 | 33.86 |

# 12.3 Obscured glass

Wired glass shall polished wire glass having both surfaces ground and polished and with hexagonal or square wire mesh inserted during rolling complying with British standard No. 952 section 4  of the substance shown below:

| Nominal substance approximate |  | Approximate weight |  |  |
| --- | --- | --- | --- | --- |
|  |  | Per foot super |  | Per metre super |
| Ins. | Mm | ibs | Oz. | Kg. |
| 1/8 | 3 | 1 | 8 | 7.32 |
| 3/16 | 5 | 2 | 8 | 12.20 |
| ¼ | 6 | 3 | 8 | 17.08 |

# 12.4 wired Glass

Wired glass shall polished wire glass having both surfaces ground and polished and with hexagonal or square wire mesh inserted during rolling complying with British Standard No. 952 Section 4, ref: 20.b. of the substance shown below:

| Nominal substance | Limits of thickness | Possible variation in weight |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Per foot super per meter supper |  |  |  |  |  |
| Inches | Millimeters | Min |  | Max |  | Min | Max |
|  |  | Ib. | Oz. | Ib. | Oz. | Kg | Kg |
| ¼ | 5.56-7.14 | 2 | 12 | 3 | 12 | 13.42 | 18.30 |

# 12.5 Heat-absorbing glass

Heat-absorbing glass shall be polished plate glass substantially opaque to infra-red radiation’s complying with British standard no. 952 section 4:

| Nominal Inches | Limits of thickness millimeters | Possible variation in weight |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Per foot super per meter supper |  |  |  |  |  |
| Inches | Millimeters | Min |  | Max |  | Min | Max |
|  |  | Ib. | Oz. | Ib. | Oz. | Kg | Kg |
| 3/16 | 3.97-5.56 | 2 | 0 | 2 | 14 | 9.76 | 14.03 |
| ¼ | 5.56-7.15 | 2 | 13 | 3 | 12 | 13.73 | 18.30 |

# 12.6 Armourpslate glass

Armourplate glass shall be toughened safety glass made of heat treated polished plate complying with British standard No. 952 section 4 ref: of 1/4in. 3/8 in. or 1/2in substance as previously given.

# 12.7 Mirror glass

Mirror glass shall be silvering duality polished plate glass silvered on one side, cooper-backed, varnished and painted complying with British standard no. 952 and 27 and of the substance previously given. Edges of mirrors shall be beveled.

# 12.8 Putty

Putty for glazing to wood shall be tropical grade glazing quality. Putty for glazing to metal shall be tropical grade metallic glazing quality.

# 12.9 Glazing beads

Wood glazing beads shall be of teak, splayed and rounded to the sizes Shawn on the drawings and neatly mitered and braided. Metal beads shall be supplied with metal windows and doors and these shall be sprung or screwed on according to design.

Workmanship

# 12.10 Glazing to wood without beads

The rebates shall be previously treated with one coat of priming paint and the bedding putty inserted. The glass shall be embedded in the putty and secured by sprigs. The front putty shall be inserted to form a triangular miter filling from the edge of the rebate to 2mm back from the dight line. The bedding putty shall be trimmed off level with the sight line to form neat back putty. When the putty has hardened sufficiently the painting shall be carried out and care shall be taken to seal the joint between putty and glass by painting up to the sight line.

12.11 Glazing to wood-with beads

The rebates shall be previously treated with one coat of priming paint and the bedding putty inserted. The glass shall be embedded in the putty and secured by the beads.

The bedding putty shall be trimmed off level with the slight line to form al neat back putty and the painting shall be carried out.

12.12 Glazing to metal-without beads

The rebates shall be previously treated either by rustproofing or priming as desced elsewhere and the bedding putty inserted. The glass shall be embedded in the putty and secured by the beads. The bedding putty shall be trimmed off level with the sight line to form shall be trimmed off level with the sight line to form a neat back putty and painting shall be carried out.

12.13 Galzing to metal – with beads

The rebates shall be previously treated either by rust proofing or priming as described elsewhere and the bedding putty inserted. The glass shall be embedded in the putty and secured by the beads. The bedding putty neat back putty and painting shall be carried out.

12.14 Glazing without putty

Where specimen, wash leather, ribbon velvet, flannel, felt, asbestos or similar materials shall be used in place of putty for internal glazing in conjunction with beads. The materials should be fitted so that it covers all parts of the glass which will be covered by the rebate and bead.

12.15 Mirrors

Mirrors shall be fixed to walls with rubber sleeves and chromium plated dome-headed screwed into prepared plugs let into walls.

12.16 Cleaning etc.

The contractor shall replace all cracked or broken glass and clean all gleaning both sides and all mirrors before handing over.

13.CARPENTRY AND JOINERY

13.1 Timber

All softwood for carpentry and joinery work shall be well seasoned, sound, bright, free form shakes, (large, loose or dead knots) wanly edges, warp, incipient decay, stained sapwood or other defects and shall be to approval of the engineer.

Timber for carpentry work shall be carefully sawn square and shall hold the full dimensions shown on the drawings. The hardwood for joinery work shall be best quality teak, well seasoned, close grained and free from all defects. The contractor shall allow for all necessary cutting timber to size and shape, for preparation of surfaces, for all fixings for properly jointing and putting together including framing, gluenotching, sinking, scribing, meters, ends, short lengths and any other sundry items of a like nature and for priming all concealed surfaces of joinery. Aluminum primer shall be applied to the backs of all door frames.

All sizes shown on drawings are finished sizes unless otherwise stated.

Timber for joinery work shall be finished wrote to the exact sizes shown on the drawing with pencil round exposed sarises and no joinery shall be built in until inspected and approved by the engineer.

The whole of the hardwood joinery shall be rubbed down to a smooth surface and left clean and ready to receive an oiled finish.

13.2 Moisture content of timber

The softwood generally shall have a moisture content limit of 12%. The hardwood shall have a moisture content limit of 10% and shall have been kiln dried.

The whole of the timber for joinery work shall be properly stacked and protected from rain and ground moisture.

# 13.3 Plywood

The plywood shall be external W.B.P quality resin bonded equal to B.S. 1455.

The minimum thickness shall be 4mm.

Plywood face veneers shall comply with B.S 1455, Grade 1.

Plywood adhesives shall comply with B.S. 1203, Grade 1.

Plywood shall be obtained from an approved source to the correct thickness specified. The contractor will not be permitted to make up the required thickness by gluing together sheets of thinner plywood.

# 13.4 Face veneers

Face Veneers shall be hard durable and capable of being finished easily to smooth surface. That shall be free from knot, worm and beetles holes, and splits, glue stains, filling or inlaying of any kind, of defects.

Face veneers shall be applied to one or more sides as described in the particular specification or shown of the drawings.

Timber for face veneers shall be as described in the particular.

13.5 Asbestos insulating board

Asbestos insulating board shall comply with B.S. 3536.

13.6 Fixings and jointing

Softwood in carpentry work shall be put together with steel nails except where described as framed when it shall be properly joined and held together with glue and steel screws. Fixings shall be stout steel nails and screws.

13.7 Doors

Joinery works shall be carefully put together and properly jointed in accordance with best practice; all joints shall be glued and screwed or doweled. Any screws appearing on facework shall have the heads let in and be pelted unless otherwise described.

Softwood fixings shall be about steel screws.

Hardwood joinery shall be put together and fixed brass cups and screws.

Cups for fixing hardwood joinery shall be cast brass cups with milled edges and shall be neatly let in to finish flush with the face of the work.

13.8 Windows and Sashes

Windows and fanlight sashes shall be framed to the size shown on the drawings. Sashes hung folding shall have meeting beads screwed on. Glazing bars if required shall be of twice rebated section.

13.9 Hatches and shutters

Hatches, shutters and similar items of joinery shall be framed to the sizes shown on the drawings.

13.10 Fly screens

Fly screens to doors shall be framed and braced with tails styles and braces and filled in with approved copper or galvanized steel fine wire mesh of 0.70mm beaded on.

13.11 Frames

Frames to doors, windows and fly screens shall be provided and built in to the sizes shown on the drawing.

Frames shall be securely tied to walls by means of steel or similar metal cramps, galvanized or dipped in bitumen as follows:

Door frames: Three cramps to each side.

Window frames: Two or more cramps to each side according to size.

Doors, windows, etc shall be carefully and accurately fitted to the frames to give a uniform clearance of not more than 3mm all round.

Architrave, door stops, etc shall be as shown on the drawings and all properly mitered at intersections.

Glazed beads where required shall be wrought splayed and rounded and shall be neatly mitered and fixed with small brads or lost-head nails.

13.12Fittings

In connection with fittings such as wardrobes, cupboards counters, ect, the doors, frames, drawers, ran a framing etc, shall be properly and accurately framed together as shown on the drawings.

13.13 Shelving

Wrought shelving shall be constructed and fitted as shown on the drawings supported with bearers on farming.

13.14 Scribing

All joinery such as architrave, beads, etc. required to fit against the contour of irregular surface shall be accurately scribed to ensure a close butt connection.

13.15 Finish

All joinery which is to be polished, varnished or painted shall be finished smoothed and clean by rubbing down with the fine sandpaper.

13.16 Protect joinery from damage

All joinery shall be protected from damage during the course of the Works and on completion shall be to the engineer's entire satisfaction. Before handing over, the Contractor shall ensure that all doors, drawers, etc. work easily and shall make all necessary adjustments including those needs during the maintenance period.

# 14.ROOF FINISHES:-

The work of roof finishes shall consist of the following:-

a) 	Hot bitumen primer coat to concrete roof slab.

b)	Thermal insulation.

c)	Sheathing membrane.

d) 	Sand/Cement screed.

e) 	Roof waterproofing and U/V protection

Contractors Obligations:-

The Contractor shall provide all the  materials, labour and equipment  etc.,  for  this  work  and  shall  carry out and complete   the  entire   work  of   roof  finishes   as  per specifications detailed below:-

# 14.1SPECIFICATIONS

a) Insulation

Polystyrene Rigid Foam Boards

Contractor  shall lay  a layer  of 5  Cm. thick rigid polystyrene boards fully bonded  to primed surface of the  screed  or  directly  on  the  concrete slabs as   specified here under.

Bonding shall  be done either by hot bitumen or any other approved bonding  agent recommended by manufacturer. Above polystyrene  rigid boards  shall comply with the following:-

Thickness                        				: 5 Cms.

Thermal conductivity at 10% mean temperature      	: K=0.028 W/m deg. C

Density                          				: 32.35 Kg./m3

Water absorption                 				: 0.1% volume

Capillary                      				: None

Compressive strength at 5% Compression                 : =0.245 M/N/M2

There shall be no air between screed or concrete slab and polystyrene board.

Polyurethane Foam:

3 Cm. thick (minimum) polyurethane foam sprayed in 3 layers each 1 cm. thick over cement/sand screed laid to fall (1%) over the primed surface of the concrete roof slab. It shall consists of the following:-

1 part 'Plyol' and 1  part 'Isocyanate' mixed as recommended by the manufacturer and approved by the Director of works or his representative.

Mixing Proportions                      	: 1/1

Density                                 		: 60 Kg./m3

##### Tensile strength                        	: 5.0 daN/cm2

Compressive strength                    	: 3.5 daN/Cm2

Water absorption                        	: 59 gr/M2/24 hours

Thermal conductivity                    	: 0.021 W C

Rigid Mineral Wool Slab:-

Rigid  mineral  wool  slabs  shall  be  bonded to the primed surface of concrete slab. The rigid mineral wool slabs shall comply with the following:-

Thickness:

8 Cms. thick faced with  aluminum foil on one side.

Non combustibles and water repellent.

Density:

120 Kg/m3

Thermal conductivity   coefficient 'K' value  at 10 C shall not be more than 0.031 w/m  deg. C. It shall be fully bonded to concrete roof slab with hot bitumen or the approved/recommended bonding agent.

b) Sand/Cement Screed:

(A base for  waterproofing  treatment  or  thermal insulation)

Minimum  3 Cm. thick sand/cement  screed layer - 1 part cement to 4 parts clear sand shall be laid to fall 1% or as specified  on the drawings, over the concrete roof slab or  the roof thermal insulation depending on the types  of roof finishes specified here under. Maximum  thickness of the  screed shall be 10 cm.

Sand used for the  screed shall be  clean natural and,  free  of  all  salts  and  other impurities, graded passing through a 4.76 mm. British Standard sieve with a good proportion of larger particles.

Cement shall be Portland cement complying to B.S. 12: 1978 for ordinary and rapid hardening Portland cement.

c) Waterproofing:

Two coats of Elastomeric Acrylic Paint

Diathon or similar approved waterproofing and ultraviolet ray's protection shall be applied over the polyurethane foam. First coat shall be gray color with fiber glass mesh reinforcement bonded to the insulation surface. The second top coat shall be white color applied perpendicular to the first coat. Total thickness of the coat shall be 609 dry microns (excluding fiberglass mesh). The above waterproofing only used when polyurethane foam insulation is used over the screed for non-traffic able roofs.

Cold  applied waterproofing membrane for non-Traffic able roofs:-

a) 2 coats of 2 component Elastomeric self adhesive membrane over primed, screeded surfaces with aluminum paint on top for U/V protection. Component Elastomeric self adhesive membrane shall consist of a mix of 9 volumes 'premix' - polymerizable black liquid and one volume of 'Activator' - straw colored liquid - laid to an average thickness of 1.5 mm. Top coat shall be sprayed with a layer of clean sand when it is still green, as a key for the U/V protection, which shall be done by two coats of aluminum reflective paint.

b) Rubberized bitumen/polyurethane membrane shall consist of standard rolls of self adhesive and self-sealing 1.5 mm. thick rubber-bitumen compound with solar shield a luminous to exposed top surface - all to be laid on primed screeded surface with necessary end laps and side laps as recommended by the manufacturers.

Traffic able Roofs:-

a) 2 components Elastomeric membrane shall have average thickness of 1.5 mm. and shall be mix consisting of 9 volumes 'Premix' - polymerizable black liquid and one volume of 'Activator' - a straw colored liquid laid over primed roof surface.

Rubberized bitumen/polythene shall consist of standard rolls of self-adhesive and self sealing bitumen/polythene waterproofing membrane to factory controlled thickness of 1.5 mm. confirming to B.S. Code of Practice 102.

b) Self adhesive membrane 4kg/m2 with angle fillet will be used as water proofing layer (polypit or approved equivalent).

Priming of Concrete Roof Slab Surfaces:

Top surfaces of roof slab shall be  primed and given two coats of Oxidized bitumen  115/15 at the  rate 2 kg./m2  brush applied  to  cover all the  surfaces - up stands,  sleeves of ducts, pipes etc., that are required to covered with roof finishes mentioned above.

Sheathing Membrane:

Unless otherwise said in the BOQ, Polythene  'Visqueen'  500 Grade  or similar membrane  laid with  necessary side laps (10  Cm.) and end laps as required (Min. 15 Cm.)

Concrete  Passing Slabs:

Pre-cast paving slabs shall be hydraulically pressed, square edges  sizes  60 x 60 5 Cm. thick made from Portland cement and aggregates-all to comply B.S. 	368:1971.

Mastic Sealant:

Mastic used for the joints shall be cold poured - 2 part  polysulphide based sealants confirming  to B.S. 4254:1967.

d) Type of Roof finishes based on the above Specifications:-

1	Roof finishes Type A:                                   (Non-Trafficable Roofs)

Step (1) : Priming of roof slab/surfaces

Step (2) : Sand/cement screed

Step (3) : Polyurethane foam

Step (4) : U/V  protective  coating/waterproofing

2	Roof Finishes Type B:            		   (Non-Trafficable Roofs)

Step  (1)  : Priming of roof slab/surfaces

Step (2) :Polystyrene rigid insulation slabs (boards) laid  over primed  surfaces of  		    roof slab

Step  (3)  : Sheathing membrane

Step  (4)  : Sand/cement screed

Step  (5)  : Waterproofing

3 	Roof Finishes Type C:                              (Non-Trafficable Roofs)

Step (1) : Priming  of  the  roof  slab  surfaces

Step (2) : Rigid  mineral  wool  insulation  slabs

Step (3) : Sheathing membrane

Step (4) : Sand/Cement screed

4	Roof Finishes Type D:                         (Trafficable Roofs)

Step (1) : Priming  of  the  roof  slab  surfaces

Step (2) : Thermal insulation

Step (3) : Sheathing membrane

Step (4) : Sand/Cement screed

Step (5) : Roof waterproofing

Step (6) : Sand/cement mortar  (1:6) bed  min. 2.5 Cm. thick			Step (7) : 5 Cm. thick  60 x 60 Cm.

5.	Contractor must use the type of finishes as specified on the drawings for the  particular project  or any  other type of roof finishes specified above and approved by the Director of works or his representative. Work of the roof finishes shall be carried  to the complete  satisfaction of  the Director of works or his representative of works or his representative. The  roof shall be tested for water tightness by flooding  the same with  5 Cm. deep sheet of water for  72 hours prior to initial take-over of the building.

6.	Contractor  must  use  the  appropriate  type of detail for horizontal and vertical joints as shown on the drawings. Up stands for expansion joints on the roof shall be properly covered with the waterproofing membrane over the plastered vertical and horizontal surfaces. Points shall be properly sealed  with approved  mastic sealants  and protected  from damage by providing pressed  aluminum  sheet  cover  as  indicated in details on  he drawings.

15. ROADS WORK

# 15.1 Earthwork And Road Excavation

15.1.1	SCOPE OF WORK

The Contractor shall include excavation as required to provide a smooth, gentle slope to meet the existing adjacent ground surface.  For the sub-grade preparation he shall scarify a layer of an adequate area and suitable depth not less than 300 mm, and the soil shall be pulverized, mixed, shaped, compacted and finished, all in accordance with the Specifications.  All materials within the top 450 mm below sub-grade level shall be an approved material of C.B.R. not less than 15% and compacted in accordance with Specifications.

Unless otherwise specified or approved by the Engineer, the excavated materials shall be used as fill material.  The unsuitable material shall be removed and the surface of the cut section shall be compacted to 95 percent of dry weight density according to ASTM D1557 Method K, to a depth of 150 mm below surface of cut before placement of approved fill material.

15.1.2	STANDARD EARTHWORK COMPACTION TEST PROCEDURE:

15.1.2.1  Test Methods:

All compacted earth fill dry density shall equal or exceed the specified percentage as determined by ASTM D1557, Method C. This method will be used to determine the maximum dry density of each type of soil used in compacted fills, backfills, embankments, and subgrades.

15.1.2.2  Compaction Tests:

During the course of the work, the Contractor, under supervision of the Engineer, will perform such tests as are required by the Engineer, to identify materials, to determine compaction characteristics, to determine moisture content, and to determine density of fill in place. These tests performed by the Contractor will be used to verify that the fills conform to the requirements of the specifications.

15.1.2.3  Testing:

Testing will be performed by qualified staff of the contractor or testing laboratory approved by the Engineer when, where, and as directed by the Engineer. The costs of all compaction testing and other tests as stated above will be borne by the Contractor. The Contractor shall adjust his operations so as to permit time to make tests, and shall excavate and fill such holes as may be required for sampling and testing.

15.1.3	PLACEMENT OF BORROW MATERIALS, BACKFILLING AND FILLING:

Where borrow or fill materials are to be placed and compacted on hillsides, or where new fill is to be compacted against existing embankments, or where fill is built one-half width at a time on slopes steeper than 3 (three) horizontal to 1 (one) vertical, the slopes of the original hillside, old or new fill, shall be cut into as the work is brought up in layers (benching) and the grades shall slope according to the Drawings.  Material thus cut out shall be incorporated and compacted with the new fill.

Borrow materials or fills shall be formed in horizontal layers of uniform thickness and the work shall be carried out to adhere to the slopes, levels, depths.  After adjustment of the moisture content to that required to attain maximum density, the loose material shall be compacted to obtain the required density.

Placement of borrow materials or fills at points inaccessible to normal compaction equipment shall be made in horizontal layers of  loose material not exceeding 100 mm  in depth and thoroughly compacted by the use of mechanical tampers.

Prior to the placement of any borrow materials, the Contractor shall construct trial compaction tests as directed by the Engineer.  The borrow material used in the trials shall be with the proposed borrow material and the compaction equipment to be used shall be that specified and acceptable to the Engineer.  The object of these trials shall be to determine the optimum moisture content and the relationship between the number of compaction equipment passes and density for the proposed  borrow materials.

The density to which  borrow material or fill layers shall be compacted is as required to comply with the requirements of Clause 2.2

Borrow material which does not contain sufficient moisture to obtain the required compaction shall have additional water incorporated therein by the use of approved sprinklers and mixing.  Material containing an excess which is  amount of moisture which is required to obtain the necessary compaction shall not, without written approval of the Engineer, be incorporated in the full until it has been allowed to dry prior to compaction.  Drying of wet material may be expedited by disking or other approved methods.

The compaction of borrow materials or fills shall be carried out at moisture content determined by the Engineer.  In forming the embankments the Contractor shall provide that the work can be drained free of rain water and the Contractor shall make allowances in the height and width of the work for any selling or shrinkage.

When an embankment or filled area has achieved settlement and requires additional material to bring it up to the required formation level, the top of the borrow or fill shall be thoroughly scarified before the placement of additional material when the depth of the additional material is less than 300 mm.

15.1.4  COMPACTION:

The Contractor shall carry out the compaction of borrow materials or fills as specified after grading and leveling the surface to be compacted in areas to be filled, compaction shall include adding necessary fill, water, and other materials as required, and compacting the first layer in addition to subsequent layers up to the proposed levels.  In areas already excavated down to the required level, compaction shall include adding the necessary water, etc., and compacting the surface, in accordance with the procedure outlined hereinafter.  The procedure outlined below shall not relieve the contractor of his duties to determine the most suitable procedure for compaction and all such procedures shall be subject to the approval of the Engineer.

After carrying out the grading, leveling, scarifying, pulverizing, and other work as required, of the fill layer to be compacted as per specifications, the Contractor shall add the necessary amount of water to permeate the pulverized fill in the quantity required, all in accordance with the directions of the Engineer.  The fill shall then be thoroughly turned over after adding each lot of water so as to achieve a homogenous moisture content in the whole thickness of the layer.

Before compacting, samples from the pulverized fill will be taken and tested according to laboratory testing, (field testing using “Speedy Moisture Device” or similar instrument giving direct readings for the filled moisture content may be used for guidance only), in order to establish the natural moisture content.  In the event that it is more than Optimum Moisture Content, the area of sub-grade represented by this sample shall be scarified and aerated until the moisture content is within minus 2 and plus 4 percent of the Optimum Moisture Content.  Then the fill shall be primarily leveled in order to commence fill compaction.

After primary leveling compaction shall be commenced by means of approved rollers depending on the type of material being compacted in order to obtain 95 percent of maximum dry density.  Placement of   borrow materials or fills shall be in layers not exceeding 150 mm compacted thickness.  When tested in place, borrow material shall have a minimum density of 95 percent of maximum dry density to a minimum depth of 300 mm below the top of sub-grade.  Borrow material shall be tested and shall have a California Bearing Ration (C.B.R) of 15 as a minimum.

The rolling shall be carried out in the direction of the road axis until the fill reaches the required density.  In crowned sections, rolling shall start from both edges of the road in the direction of the axis .  If the road is super elevated, rolling shall commence from the lower side and continue to the higher side.  In order to compensate for the amount of water lost in evaporation in the course of compaction, additional quantities of water shall be added as required.

The surface shall thereafter be leveled longitudinally and transversely by motor graders and finally rolled to achieve uniform compaction free from undulations, soft spots and depressions.

15.1.5  SUB-GRADE PREPARATION:

All sub-grade material within the upper 450 mm below the top of sub-grade elevation shall have a minimum California Bearing Ratio (C.B.R) of 15 when tested in accordance with AASHTO T-193.  When the upper 450 mm below the sub-grade elevation of earth cut is found to be incapable of compaction as specified such sub-grade material shall be removed and replaced.

After the foregoing work has been accomplished, the entire sub-grade shall be shaped to a smooth uniform surface.  Excess material which cannot be disposed of any normal drifting to the low spots during blading and shaping operations shall be removed and disposed of by placing it in sub-grade areas deficient in materials, and shall be watered and compacted as necessary to yield a true finished sub-grade as described above.

Once prepared, the sub-grade shall be maintained in the finished condition until the first succeeding course of sub-base or base material has been placed.   The Contractor shall take all  precautions necessary to protect the sub-grade from damage; hauling over finished sub-grade shall be limited to that which is essential for construction purposes.  The Contractor shall protect the prepared sub-grade from both his own and public traffic. The Contractor shall maintain the sub-grade by blading and rolling as frequently as may be necessary to preserve the sub-grade in a completely satisfactory condition.

15.1.6  NATURAL SUBBASE COURSE (KURKAR)

11.1.6.1 Scope

The work covered by this article of the Technical Specifications consists in furnishing all plant, labor, equipment and materials and in performing all operations in connection with the complete construction of a soil aggregate sub-base on a prepared subgrade, in strict accordance with this Section of the Technical  Specifications and in conformity with the lines, grades, thickness and typical cross-sections shown on the Drawings or as directed by the Engineer.

11.1.6.2  Materials in General

The Natural Sub-base Course shall consist of the material hereinafter specified, placed and compacted on a previously prepared sub-grade.

A) Grading

The Natural Subbase Material (Kurkar), shall conform to the grading shown in the following Table and be subject to the approval of the Engineer.

| Sieve Size (Square Openings) |  | Percentage by Weight Passing Square mesh Sieves |
| --- | --- | --- |
| 1” |  | 100 |
| 3/8” |  | 60-100 |
| No. 4 | (4.76 mm) | 40-80 |
| No. 10 | (2.00 mm) | 20-70 |
| No. 40 | (420 micron) | 10-50 |
| No. 200 | (74 micron) | 5-35 |

The fraction passing the No. 200 sieve shall not be greater than two thirds of the fraction passing the No. 40 sieve.

The above grading requirements do not apply to materials which their gradation when tamped.

B) Specific Gravity

The specific gravity of aggregates shall not be less than 2.40.

C) Liquid Limit and Plasticity Index

The liquid limit and plasticity index requirements stated herein shall apply to any component which is blended to meet the required gradations and also to the completed course.  The portion of any component or of the completed course passing the No. 40 sieve shall be non-plastic or shall have a low  liquid limit and plasticity index.  In no case will material be permitted which has a liquid limit in excess of 40 or a plasticity index in excess of 10.

D) California Bearing Ratio

The C.B.R Index determined on a remolded sample according to ASTM D 1557 , and after soaking in water for 4 days, following ASTM D 1883 shall not be less than 20%, when compacted at the maximum density and optimum moisture content.  The Index shall not be reduced by more than 5% for a compaction moisture of the sample of  2% of the moisture content to obtain the maximum C.B.R.

E) Sampling, Testing and Approving

All samples of aggregates shall be Supplied by the Contractor at his own expense.  All test  necessary to determine compliance with requirements specified herein shall be performed by the Contractor at his own expense.

The source of the materials to be used for producing the aggregates shall be selected well in advance of the time they will be required in the work.

Tentative approval tentative final disapproval of a source of a material will be pronounced on the basis of inspection of the source by a representative of the Engineer, plus tests made on samples submitted by the Contractor from test pits, borings, or other excavations or from samples of current production in the case of an existing producer.  Samples of the size required shall be submitted by the Contractor not less than 30 days prior to commencing work. Approval or disapproval of the source from the standpoint of all requirement grading, liquid limit, and plasticity index will be pronounced on the basis of tests and on samples obtained from production for the specific job.  Samples of the aggregates shall be furnished by the Contractor at regular intervals during production as required by the Engineer.  These samples will be obtained at the processing plant, trucks, stock-piles, or from other locations designated by the Engineer, and will be basis for disapproval of specific lots or for the approval of specific lots from the standpoint of all requirements grading, liquid limit and plasticity index.  When deemed necessary, the sampling of materials will be observed and supervised by the Engineer.   The completed subbase course layer is defined as subbase course layer which is ready for the next layer.  These samples will also be obtained under the supervision of the Engineer.  Unless otherwise directed by the Engineer, the Contractor, will follow procedures outlined in ASTM D 75 for sample of the materials.

11.1.6.3  Equipment

The Contractor shall provide all plant, equipment, tools and machinery necessary to perform the works covered by this Division of the Technical Specifications in a proper way and in accordance with these Technical Specification.

All plant, equipment, tools and machines used in the performance of the work covered by this Section of the Technical Specifications, shall be approved by the Engineer prior to commencement of work and shall be maintained in satisfactory condition at all times.

The equipment and plant shall consist of but not be limited to static and vibrating rollers, black graders, rubber-typed rollers, sprinkling equipment, spreaders, tampers, and other equipment suitable for constructing the natural subbase course.

15.1.6.4  Operations of Pits and Quarries

All work involved in the clearing, stripping and excavating in the opening or operation of pits or quarries shall be performed by the Contractor.

The pits or quarries shall be opened in such a manner as to expose the vertical faces of the deposit for suitable working depths.  Materials excavated from pits shall be obtained in successive vertical cut extending through all exposed strata.

All pockets or strata of unsuitable materials overlying or occurring in the deposit shall be wastes directed by the Engineer.  The methods of operating the pits or quarries, and the processing and blending of the material, may be changed or modified by the Engineer without adjustments in the unit rates, when such action is necessary in order to obtain material conforming to the specified requirements.

15.1.6.5  Stockpiling Material

Material shall be stockpiled in such a manner as to avoid segregation and at suitable locations designated by the Engineer.  Prior to stockpiling or material, the storage sites shall be cleaned and leveled by the Contractor.

15.1.6.6  Forms

Side forms, if used, shall be wood or metal of  a depth equal to that of the spread layer or loose materials.  The forms shall be set true to the required line and grades with their ends securely fastened together and shall be securely staked.

15.1.6.7  Preparation of  Subgrade

Prior to constructing the Natural Subbase (Kurkar), the previously constructed subgrade  shall be cleaned of all foreign substances.  The surface so prepared will be inspected by the Engineer for adequate compaction and surface tolerances.

15.1.6.8  Grade Control

The finished and completed subbase (Kurkar) shall conform to the lines, grades, cross-sections, and dimensions shown on the Drawings.

Lines and grade stakes shall be placed by the Contractor at the site of the work as directed by the  Engineer.

15.1.6.9  Compaction

Each layer of the natural subbase shall be compacted with power rollers and heavy rubber-typed rollers as approved by the Engineer.  Water content shall be maintained during the compaction procedure at optimum or at the percentage specified by the Engineer.  In all places not accessible to the rollers, the mixtures shall be compacted with mechanical tampers.

Compaction shall continue until each layer is compacted  through the full depth to at least 100% of the maximum density obtained by ASTM D 1557, Method D.

Field densities will be measured on the total sample.  The surface of each layer shall be finished by blading and rolling with power rollers, rubber-typed rollers, or combinations thereof.  The Contractor shall make such adjustments in rolling or finishing procedures as may be required to obtain true grades, to minimized segregation and degradation, to reduce or accelerate loss or grain of water, and to insure a satisfactory soil-aggregate sub-base course.

Any materials which are found to be unsatisfactory will be removed and replaced with satisfactory material or reworked to produce a satisfactory material.

15.1.6.10  Edges of Subbase

A) With Side Forms

After removing the forms, if used, the space between the compacted natural subbase course and the earth backing shall be filled with approved material in such quantity and to the height that will compact to the final thickness of the course being constructed and allow at least a 30 cm. width of the shoulder to be rolled and compacted therewith to the satisfaction of the Engineer.

B) Without Side Forms

Approved material shall be placed along the edges of the natural subbase in such quantity as will compact to the thickness of the course being considered or, when the course is being constructed in two or more layers, to the thickness of each layer of the course, allowing in each operation at least a 30 cm. width of the shoulder to be rolled and compacted simultaneously with the rolling and compacting of each layer of the subbase course, as directed by the Engineer.

15.1.6.11  Smoothness Test

The surface of each layer shall not show any deviations in excess of 1.0 cm. when tested with a 3 meters straight-edge applied parallel with and at right angles to the centerline of the paved area.  Any deviation in excess of this amount shall be corrected by the Contractor by removing material, replacing with new material or reworking existing material and compacting as directed by the Engineer.

15.1.6.12  Thickness Control

The completed thickness of the natural subbase shall be within 1 cm. plus or minus of the thickness shown on the Drawings.  The thickness of subbase course shall be measured at intervals in such a manner that there will be thickness measurement for at least each 1000 sq.m. of subbase.  The thickness measurement shall be made by test holes, at least 7.6 cm. in diameter through  the subbase course.  Where the measured thickness of the subbase is more than 1 cm. thicker than shown on the Drawings. the Contractor shall correct at his expenses such areas by scarifying, adding or removing mixture, re-blading and re-compacting as directed by the Engineer.

The average job thickness shall be the average of the job measurements determined s specified above  but shall be within 0.5 cm. plus or minus of the thickness shown on the Drawings.

15.1.6.13  Maintenance

The Natural subbase shall be maintained by the Contractor in a condition satisfactory to the Engineer until the completed work is accepted.

# 15.2sub-Base And Base Courses

15.2.1	General:

Locating sources and manufacturers of materials are the responsibility of the contractor.

Prior to starting quarry or borrow pit operations, the contractor shall obtain written permission from the Authorities or Owner concerned.

The contractor shall submit to the Engineer, 10 days prior to the scheduled beginning of crushing and screening, a statement of origin of all stone and/or gravel aggregates and granular materials.

The contractor shall submit for testing and approval, representative samples of all materials needed. Samples shall be taken by the contractor in the presence of the Engineer. Approval of specific sources of materials shall not be construed as final approval.

The contractor may conduct necessary tests in the Field Laboratory in the presence of the Engineer and the contractor’s Materials Engineer.

Samples shall satisfy all specified test requirements. The contractor shall furnish all necessary labor, transport, tools and equipment required by the Engineer.

15.2.2	Granular  Material  For Sub-Base:

15.2.2.1 Granular material for use in sub-base courses, shall be a naturally occurring gravel, blended as necessary with fine or coarse material and screened to produce the specified gradation. Crushing of natural granular material shall not normally be required, unless for the purpose of meeting the gradation requirements, or when shown on the Drawings (to produce a higher quality sub-base with improved mechanical stability).

15.2.2.2 Gravel shall consist of hard durable and sound stones, free from deleterious substances not mentioned below.

Other requirements are:

Crystalline gypsum (expressed as SO3) 	5% max.

Clay lumps and friable particles 		10% max.

Flakey and elongated particles as follows:

Crushed rock					40% max. each

Crushed gravel 				45% max. each

Natural gravel 				50% max. each

Determined in accordance with BS812 Section 105.1: 1985 and BS812 Part 1 1975)

Maximum dry density (gm/cm3): 2.05 min.

Chert content ( determined by percentage by  weight insoluble in hydrochloric acid) to be specified in special technical  specification.

15.2.2.3 Granular materials delivered to the road site shall meet the requirement of class A or B as shown in Table 3.1, when tested in accordance with AASHTO T-27 after dry mixing and just before spreading and compacting.  The Class of granular material to be used shall be as shown on the Drawings or otherwise as selected by the Engineer. The actual gradation shall, in all cases, be continuous and smooth within the specified limits for each Class. If gradation is tested after compaction, a tolerance of 3% is allowed in the upper limit for the percentage of material passing sieve no. 200.

Gradation of Granular Material by Class

|  | Percent by weight passing |  |
| --- | --- | --- |
| Sieve Designation (Square openings) | Class A | Class B |
| 63mm (2-1/2 in.) | 100 |  |
| 50mm (2 in.) | 80-100 | 100 |
| 37.5mm (1-1/2 in.) | 70-95 | 80-100 |
| 25mm (1 in.) | 55-90 | 60-95 |
| 12.5mm (1/2 in.) | 45-75 | 47-80 |
| 4.75mm (No.4) | 30-60 | 30-60 |
| 2.00mmm (No. 10) | 22-48 | 22-45 |
| 0.425mm (No.40) | 10-30 | 10-30 |
| 0.075mm (No. 200) | 5-12 | 5-12 |

15.2.2.4 The material shall contain a minimum of 25% sand equivalent at any stage of  construction.

15.2.2.5 The loss weight of granular material shall not exceed 45% after 500 revolution, when tested in accordance with AASHTO T 96 (Los Angelos Abrasion Test).

The ratio of wear loss = Abrasionafter100Rev.Abrasionafter500Rev.

should not be more than twenty percent of the maximum allowed abrasion after 500 revolution.

15.2.2.6 The granular martial shall have after 4-day soaked CBR of not less than 30% when compacted at 100% of modified proctor AASHTO (T 180-D) and tested in accordance with AASHTO T 193.

15.2.2.7 When tested for soundness in accordance  with AASHTO T 104, the material shall not show signs of disintegration and the percentage loss in weight after 5 cycles shall not exceed 12% in the case of the sodium sulphate test and 18% in the case of the magnesium sulphate test.

15.2.2.8 The portion of granular material, including any blended material, passing the 0.425 mm (No. 40) mesh sieve shall have a liquid limit (L.L.) of not more than 30% and a plasticity index (P.I.) shall neither be less than 2 nor greater then 8 when tested in  accordance with AASHTO T 89 and T 90.

Non Plastic condition might be accepted if crushed lime stone is used provided that angularity test (R) value shall not be less than 8.

If additional fine material is required to correct the gradation of the granular material, or for adjusting the L.L. or P.I. of the fraction passing 0.425 mm (No. 40) sieve, it shall be uniformly blended and mixed with the granular material. Additional fine material for these purposes shall be obtained from the crushing of stone, gravel, or slag, if naturally occurring fine material is not available.

15.2.3	Aggregate For Base Courses:

Aggregate for use in base course construction shall be crushed stone, and may be washed, if directed, to remove excessive quantities of clay, silty clay or salts.

It shall consist of  hard durable and sound particles or fragments of stone, free from other substance.

Other requirements:

Gypsum content (expressed as So3) 2 % max.

Clay lumps and friable particles8 % max.

Elongated and flakey particles for crushed  rock (Determined in accordance with  BS 812 Part  1: 1975)

Granit and Basalt			40 % max each.

Lime stone				35 % max

Maximum dry density (g/cm3)	2.1 % min

Gradation of Base course Aggregate by class

|  | Percent by weight passing |  |
| --- | --- | --- |
| Sieve Designation | Class A | Class B |
| 50 mm ( 2 in ) |  | 100 |
| 37.5 mm ( 1.5 in) | 100 | 70-100 |
| 25 mm (1 in ) | 75-100 | 55-85 |
| 19 mm (3/4 in ) | 60-90 | 50-80 |
| 12.5 mm ( 1/2 in ) | 45-80 |  |
| 9.5 mm (3/8 in ) | 40-70 | 40-70 |
| 4.75 mm (No 4) | 30-65 | 30-60 |
| 2 mm (No 10) | 20-40 | 20-50 |
| 0.425 mm (No 40) | 8-20 | 10-30 |
| 0.075 mm (No 200) | 5-10 | 5-15 |

The material shall contain a minimum of 35 % sand equivalent at any stage of construction.

The loss weight shall not exceed 45 % after 500 revolution, when tested in accordance with AASHTO T96 (Los Angeles Abrasion Test).

The ratio of wear lossAbrasionafter100Rev.Abrasionafter500Rev., should not be more than twenty percent of maximum allowed abrasion after 500 revolution.

The crushed aggregate base course material shall have a 4-day  soaked CBR of not        less  than 80 when compacted at 100 % of modified proctor AASHTO (T 180-D) and tested in accordance with AASHTO T 193.

When tested for soundness is accordance with AASHTO -104, the material shall not show signs of disintegration and the loss by weight shall not exceed 12 % in case of the sodium sulphate test, and 18 % in the case of the magnesium sulphate test.

The portion of aggregate, including  any blended material passing the 0.425 mm (No 40)  sieve shall have a liquid limit (L.L.) of not more than 25 and plasticity index (P.I) of not more than 6 when tested in accordance with AASHTO T 89 and T 90.

If additional fine material is required to correct the aggregate gradation or for adjusting the L.L or P.I. of fraction passing the 0.425 mm (No 40) sieve, it shall be uniformly blended and mixed with the aggregate material.

15.2.4	GRANULAR SUB-BASE COURSES

15.2.4.1 Scope:

These Works shall consist of furnishing granular sub-base material of the required Class, mixing, spreading on prepared subgrade, compacting and finishing, all as and where shown on the Drawings.

15.2.4.2  Materials

All materials shall confirm with the relevant requirements of Section "Materials", in respect of granular material Class A or Class B for sub-base construction.

15.2.4.3  Subgrade Surface Preparation

The subgrade shall have previously be constructed in accordance with the requirements of  Section   "Subgrade Construction and Topping" and properly maintained and kept well drained thereafter.

At all special grade control points, such as at bridge structures, existing pavements, the subgrade shall be lowered to a depth sufficient to permit construction of the sub-base course to the specified elevations and thickness.

Transitions shall be of sufficient length to avoid abrupt  change of grade and shall be within plus or minus 3% of the final design grade unless otherwise directed. Surplus material shall be removed and disposed off.

The subgrade shall be inspected and approved immediately prior to commencement of sub-base construction. Any soft, yielding material shall be removed and replaced by approved topping material. Holes, depression and other irregularities shall be made good as directed and the subgrade re-compacted as necessary and finished ready to receive the sub-base course.

15.2.4.4 Equipment

Equipment used to handle, place, spread, water, compact and finish sub-base shall conform with the requirements of Section  "Contractor's Plant and Equipment" and with the Contractor's approved Work Program.

15.2.4.5 Construction

a) Stockpiling of Granular Material:

Stockpiling procedures shall conform with the relevant requirements of Section   "Materials".

Methods used for stockpiling granular material and removing it from stockpiles shall not result in significant degradation or segregation nor the introduction of significant amounts of foreign materials or extraneous matter.

Granular material adversely affected, in the opinion of the Engineer, by stockpiling or handling procedures, shall be incorporated in the Works regardless of previous approval of such material, until the deficiencies have been rectified in an acceptable manner.

b) Mixing and Spreading

All components of sub-base course material shall be mixed thoroughly and uniformly with water in situ. The amount of water added, as approved by the Engineer, shall be such that the material will be uniform and within the specified moisture content range at the time of compaction.  Wetting of granular material in stockpiles or in trucks before or during delivery to the site will not be permitted. However, water shall be added to the material, if necessary, during placing and compaction of sub-base material.

The sub-base material shall be placed on the subgrade in a uniform  two layers  each 150 mm thickness ( after compaction).

If approved, heavy duty vibratory compaction equipment is used, the subbase  may be in one 300 mm layer (after compaction) provided compaction tests with appropriate testing equipment indicate that the specified compaction standard will be attained and uniform throughout the thickness.

The sub-base material shall be placed to the required width using a self-propered spreader or motor grade equipped with blade extensions. Water shall be applied by approved spraving equipment and thoroughly mixed with the sub-base material.

The material shall not be bandled in such a way as to cause segregation. If the spreading equipment causes segregation in the material, or leaves ridges, or other objectionable  marks on the surface which cannot be readily eliminated or prevented by adjustment of the equipment, the use of such equipment shall forthwith be discontinued and it shall be replaced by a spreader or grader capable or spreading the material in proper manner.

All segregated material shall be removed and replaced with well-graded material.  "Skin" patching will not be permitted.  Only minor surface manipulation and watering to achieve the required surface tolerances will be permitted during the compaction process.

Neither hauling nor placement of material will be permitted when, in the judgement of the Engineer, the weather or surface conditions are such that hauling operations will cause cutting of the subgrade or cause contamination of the sub-base material.

c) Compaction

The Contractor shall plan the sequence of operations so that the least amount of water will be lost by evaporation from uncompleted surfaces, If the Contractor delays placing of succeeding layers of material to the extent that  additional water is required to prevent raveling or excessive drying, the application of such water shall be carried out  as directed and at the Contractor's expense.

The sub-base material shall be compacted by means of approved compaction equipment, progressing gradually from the outside towards the center, with each succeeding pass uniformly overlapping the previous pass.

Rolling shall continue until the entire thickness of each sub-base layer is thoroughly and uniformly to 100% AASHTO T 180 (Method D) maximum density. Final rolling of the completed course shall be means of an approved self-propeled roller. Rolling shall be accompanied by sufficient blading, to insure a smooth surface, free from ruts or ridges and having the proper shape. When additional water is required, it shall be applied in an approved manner.

Any areas inaccessible to normal compaction shall be compacted by use of portable mechanical tampers until the required standard of compaction is achieved.

Each layer shall be completely compacted and approved prior to delivery of materials for the subsequent layer.

Prior to placing a subsequent layer, the existing surface shall be made sufficiently moist as directed, to ensure proper bond between the layers.

The edges and slopes of the sub-base course shall be bladed or otherwise dressed to conform to the lines and dimensions shown on the Drawings and to present straight, neat lines and slopes as free of loose material as practicable.

Material which has dried out prior to final compaction, or which has dried and re-compacted subsequent to final compaction, shall be watered and re-compacted using approved equipment and procedure. If the Contractor is unable to return the material to its original or specified condition with respect to compaction, thickness and surface tolerances, the Contractor shall remove the material and reconstruct the sub-base course on a re-approved subgrade.

d) Tolerances

The fully compacted and completed sub-base course shall conform to the lines, grades and cross sections as shown on the Drawings.

The elevations of the finished sub-base course shall be checked by the Contractor in the presence of the Engineer at maximum intervals of 10 m and at intermediate points as directed.

The tolerance on elevations of finished surface shall be plus 10 mm to minus 20 mm, minus tolerance shall be compensate by the proceeding layer.

When the finished surface is tested with a 3 m long straighedge, placed parallel to, or at right angles to the centerline, the maximum deviation of the surface from the testing edge between any 2 contact points shall not exceed 10 mm.

All areas which exceed the specified tolerances shall be corrected by removing the defective sections of sub-base and reconstructing them or, if approved, by adding new material mixing and recompacting and finishing to the specified standard.

e) Maintenance of Completed Sub-base

Following completion and acceptance of the sub-base course, it shall be maintained by the Contractor at his own expense. The sub-base shall be bladed, broomed and otherwise maintained, keeping it free from raveling and other  defects until such time as the base course is placed. Water shall be applied at such times and in such directed by the Engineer.

15.2.4.6   Testing

Every 500m of sub-base material or whenever there is a change in the material source  shall be subject to a full set of tests after mixing in situ and, if found satisfactory, shall be approved for compaction. This approval shall not deemed to constitute acceptance of the sub-base course.

Sampling and testing shall conform with the relevant requirements of Section 1.05- "Control of Materials and Standards for Sampling and Testing".

Compaction shall be tested in accordance with AASHTO T 191 or AASHTO T 205. If there is a delay between the construction of any layer and the following layer, if necessary and required by the Engineer the compaction of the lower layer may be reverified to ensure that it has not loosened due to traffic, passage of construction equipment, adverse weather conditions or otherwise.

15.2.5	AGGREGATE BASE COURSES

15.2.5.1 Scope:

These works shall consist of furnishing crushed aggregate basecouse material of class (A or B), mixing , spreading, compacting and finishing, all as and where shown in the Drawings.

15.2.5.2 Surface Preparation:

The subgrade surface shall be inspected and approved prior to commencement of base construction, Holes, depressions and other irregularities shall be made good as directed an the subgrade re-compacted as necessary and finished ready to receive the base course layer.

15.2.5.3 Equipment:

Equipment used to handle, place, spread, water, compact and finish base course in accordance with contractor’s Work program approved by the Engineer.

15.2.5.4 Construction:

Stockpiling method of aggregates and moving them from stockpiles shall not result in significant degradation nor the introduction of significant amounts of foreign materials. Aggregate materials adversely affected, in the opinion of the Engineer, by stockpiling or handling procedures, shall not be incorporated in the works regardless of previous approval of such material until the deficiencies have been rectified in an acceptable manner.

15.2.5.5 Mixing and Spreading:

Base course material shall be mixed with water to reach the specified moisture content range at the time of compaction. The mixed material shall be handled  and placed on subgrade in a uniform layer as to not  cause segregation. All segregating material shall be removed and replaced with well-graded material, ”Skin” patching will not be permitted and spread to the required width and shall be delivered such that it is ready for compaction without farther shaping.

15.2.5.6 Compaction:

The contractor shall plan the sequence of operations so that the least amount of water will be lost by evaporation from uncompleted surfaces.

The base course material shall be compacted by means of approved compaction equipment, progressing gradually from the outside towards the center, with each succeeding pass uniformly overlapping the previous pass.  Rolling shall continue until the entire thickness of each base layer is thoroughly and uniformly compacted to 100% AASHTO T 180 (Method D)  maximum density:

The edges and edge slops of the base course shall be bladed or otherwise dressed to conform to the lines and dimension shown on the Drawings.

Materials which has dried out prior to final compaction, or which has dried and decompacted subsequent to final compaction, shall  be watered and recompacted.  If the contractor failed to return the material to its original or specified condition with respect to compaction, thickness and surface tolerance the contractor shall scarify the material and  reconstruct the base course on a re-approved subgrade surface or to the satisfaction of the Engineer.

15.2.5.7   Tolerances:

- The dully compacted base course shall conform to the lines, grads and cross sections as shown in the drawings.

- The elevations of base course shall be checked at intervals of 20 m on straight and 10 m on curves, the tolerance on elevations of surface shall not exceed +10 mm or -15 mm, and not exceed 12 mm between any two contact points tested with a 4 m long straight edge placed parallel to, or at right angles to center line.

All areas which exceed the specified tolerances shall be scarified and corrected to specified standard.

15.2.5.8 Maintenance of Completed Base Course:

Following completion and acceptance of base course, it shall be maintained by contractor at his own expense. The surface shall be broomed and rolled keeping it free from defects until such time as the following course is placed. Water shall be applied at such times and in such quantities as directed.

15.2.5.9 Testing

Sub-base and base Course material shall be tested in accordance with the table shown below at stock pile and at the mixing plant for control on site tests, and if satisfactory shall be approved for use. This approval shall not be deemed to constitute acceptance of base course for full payment purposes.

Required Tests and Minimum Repetition for Base course material

| Source of Materials |  | Control on Site (The Road) |  |
| --- | --- | --- | --- |
| Required Test | Repetition Required for all Test | Required Tests | Repetition Required for all Test |
| 1- Gradation of materials | * Test for each source | 1. Proctor | * test for every 500 Lm for each layer |
| 2- Plasticity Index | * for every 2000 cm.m | 2. Gradation of materials | * when materials changed |
| 3- Abrasion | * When materials changed | 3. Plasticity Index |  |
| 4- C.B.R. |  | 4. C.B.R. |  |
| 5- Sand equivalent |  | 5. Abrasion |  |
| 6 - Percentage of Fractured Grains |  | 6. Sand equivalent 7. Clay Lumps & Friable particles 8. Field Density 9. Thickness |  |

* Test for every 750 sq.m

# 15.3 Concrete Block Paving

15.3.1 FORM OF CONSTRUCTION

Concrete block surfacing shall consist of precast concrete blocks on a laying course 50mm thick sand on sub-base on subgrade.

15.3.2 TEST STANDARDS

Unless stated otherwise, testing of subgrade, sub-base materials and workmanship shall be carried out in accordance with BS 812 and BS 1377, Laboratory Maximum Dry Density tests shall be in accordance with Test 13 of BS 1377 and liquid limit shall be determined in accordance with test 2A or 2B of BS 1377, In-situ C.B.R testing shall be in accordance with Test 15 BS 1377.

15.3.3 SUBGRADE

Subgrade shall consist of approved granular material compacted to 95% of the laboratory maximum dry density , The C.B.R value shall not be less than 95% ( in case of supplying imported fill material )

15.3.4.  SUB-BASE MATERIAL

Sub-base material shall be crushed rock or similar hard material or naturally occurring gravel which is clean and free from organic matter, clay balls and other deleterious materials, The materials shall comply with the following grading :-

| sieve size (mm) | Percentage by weight Passing |
| --- | --- |
| 75 | 100 |
| 37.5 | 85-100 |
| 10 | 40-70 |
| 5 | 25-45 |
| 0.600 | 8-22 |
| 0.075 | 0-10 |

The total acid-soluble sulphate content ( as S03 ) (BS 812 Test 118) shall not exceed 2% by weight, The total acid-soluble chloride content (as NaC1) (BS 812: Test 117) shall not exceed 3.3% by weight.

The laboratory C.B.R value shall be a minimum of 60% at 95% of the laboratory maximum dry density after soaking for 96 hours.

Material for Sub-base shall have physical Properties which do not exceed the following test value:

Liquid limit 			25%

Linear shrinkage 		3%

Plasticity index 		6%

Stone size 			50mm

Aggregate crushing value 	25%

Water absorption 		2%

Flakiness index 		35%

Elongation index  		35%

Soundness

( 5 cycles ) ( ASTM C 88 ) 	15%

The sand equivalent shall not be less than 45 when tested in accordance with ASTM D24419.

15.3.5 LAYING COMPACTION OF AND TESTING SUB-BASE

Sub-base material shall be spread evenly and compacted in layer not exceeding 200mm compacted thickness to obtain a well-bound surface finish, loose or segregated areas shall be made good by addition of lines or by removal and replacement of the material as directed.

Compaction shall be carried out by approved plant operating on the material at an approved moisture content until a dry density of not less than 98% of the laboratory maximum dry density is achieved.  One density test shall be carried per 250m2.

The sub-base shall be laid to the level shown on the Drawings the rate of one set of tests for each 500m2. The set contains of 3 sand cones tests.

The edge restraints to the paved area shall be installed before the laying course.

The sand shall be laid at a uniform moisture content and carefully screened to form a smooth compacted surface.

The profile of the laying course before compaction shall be similar to that of the finished surface, The maximum deviation from the design levels shall be + 5mm.  The laying course shall be placed to a level which takes into account the compaction which occurs during vibration of the blocks ; the amount of this compaction shall be determined by trials prior to commencement of surfacing.

15.3.6  SURFACE COURSE

The surface course shall consist of approved precast concrete blocks complying with BS6717: part 1.  The concrete constituent shall comply with the requirement of the concrete specification given elsewhere.

Additional requirements are contained in the following Clauses of this specification.

15.3.7  FINE AGGREGATE

Fine aggregate shall not contain more than 25% by weight of soluble calcium carbonate in either the fraction retained on or the fraction passing a 600 micron BS sieve.

15.3.8  COARSE AGGREGATE

Coarse aggregate shall be material retained on a 4.75mm BS sieve, the nominal maximum size shall be 10mm, The grading shall comply with BS 882, Table 4 so that when mixed with sand and cement a high density concrete is produced.

15.3.9  SAMPLING AND TESTING

Sampling and testing of blocks shall be carried out in accordance with BS 6717.  Sampled blocks shall be subjected to all the tests covered by appendices A and B of BS 6717.

If any of the 20 test blocks do not comply with the requirements for dimensional accuracy the whole consignment may be rejected.

15.3.10 TEST FOR COMPRESSIVE STRENGTH

Testing of blocks for compressive strength shall be carried out in accordance with appendix B of BS 6717 except that blocks shall be soaked for 24 hours in fresh water at 20 degrees centigrade immediately prior to testing Fresh plywood packing shall be used for each specimen tested.

15.3.11  WATER ABSORPTION

Blocks shall be tested for water absorption , The test shall be based on that specified in BS 1881 : Part 122 and the maximum acceptable limits for water absorption.

2.5% absorbed after 10 minutes.

5.0% absorbed  after 24 hours.

The acceptable limits for water absorption may be required to be varied to achieve the minimum absorption compatible with the aggregate approved for use in the paving blocks.

15.3.12  COLOR

The color of blocks shall be uniform and as detailed on the drawings or as directed, Samples of each different color shall be submitted for approval.

15.3.13  BLOCK LAYING

Block laying shall commence at angles to the main pavement axis starting at one end of the area.

Interlocking blocks shall be laid in a herringbone pattern at 45 degree to the main pavement axis or other pattern as approved or directed, Rectangular blocks shall be laid in patterns as directed using different colors if directed.

Blocks shall be laid on the sand laying course so that blocks already laid are not distributed, Blocks shall be placed to fit closely together, the width of joints shall not exceed 3mm.

Dimensional accuracy, uniformity of  joint  gaps, alignment and squares shall be checked after laying the first three rows of blocks and thereafter at regular intervals.

If joints begin to open, the blocks shall be knocked together using a hide mallet.

15.3.14  EDGE DETAILS

Special edge blocks shall be used on all edges of interlocking block paving which are parallel to or perpendicular to the main pavement axis,

Where the shape or dimensions of paved areas preclude the use of special or standard blocks on all edges, cut blocks shall be used , Blocks shall be cut to suit, using a mechanical block splatter, In-situ concrete shall not be used to make up to edge restraints.

15.3.15  COMPACTION BY VIBRATION

Blocks shall be compacted to the required levels using a plate vibrator as each area of 20 m2 is laid.

The plate vibrator shall have a plate area of 0.2 to 0.3m2 and compaction force of 9 to 16KN.  Two passes of the plate vibrator shall be made in two directions at 90 degrees to each other.

15.3.16  FILLING JOINTS

Joints shall be filled by brushing in line dry sand with a particle size up to 2mm and maximum sulphate content (as S03) of 0.4% by weight a further pass of the plate vibrator shall be made in each direction.

Weed killer have to be mixed with residual qualities with the sand used for sealing the joints.

The vibrator shall not be used within 1m of an unrestrained edge.  Paving shall not otherwise be left uncompleted overnight.

15.3.17  LAYING TOLERANCE

The finished surface level shall be within 5mm of the design level and the maximum deviation within the compacted surface, measured by a 3m straight edge shall not exceed 5mm.  The level of any two adjacent blocks shall not differ by more than 2mm.

15.3.18  LAYING COURSE

This is a 50mm thick layer of clean sharp sand containing not more than 3% silt and clay. and with not more than 10% by weight retained on a 5mm sieve.  For best results, the moisture content of the laying course sand should be within 1% of the optimum, as determined be Test 12 of  BS  1377.

The sand should be spread over the area to be paved.  The actual thickness will vary according to the tolerance of the Sub-base layer.  Sub-bases Specification are allowed a tolerance of ▒25mm.

15.3.19  COMPRESSIVE STRENGTH

The average compressive strength of the Block on delivery when sampled and tested in the manner described in item No. 511 shall not be less than 40N/mm2 in wet condition.

15.3.20  TILES ( SIDE WALK TYPE )

Tiles shall be formed as following:-

Top layer (wearing): Portland cement, quarts, bazelt gravel and coloring agent (10mm min).

Down layer: Cement, crushed sand and gravel.

Tiles shall be cured by totally immersing them after initial set has taken place in a tank of clean water for at least 24 hours.

Tiles shall be grouted upon completion, care being taken to fill all jointing completely, the grout shall consist of neat cement of a color to match the Tiling.

Dimension of tiles :- 30 x 30 x 3.2 cm

Tiles shall comply with the following Dimensioning requirements:

Deviation

-  (length , Width)	▒2mm

-  Thickness		max 2.0mm

Plainness

- Concave		max 2.0mm

- Convex		max 2.0mm

Perpendicularly (%)	max 0.5

Straightness (%)		max 0.5

Rupture Load		3000 N

Wearing Layer		▒2mm

Abrasion rate		max (3.0)mm

2.0cm Expansion joint filled with performed Bituminous Filler and sealed with cold-applied joint-sealer is to be installed / 10.0mr.

A well compacted base-course of approved materials as per specifications in section one is to be spread as a bedding layer prior to subsequent tiling.

# 15.4 Bituminous Construction

15.4.1  Material:

15.4.1.1 Scope:

All material sources and the quality of materials proposed for use in the works shall be approved prior to procurement or processing material from such sources.  Inspection, sampling , testing and re-testing as necessary, shall be at the contractors expenses.

15.4.1.2  Sampling and Testing of Aggregate:

- In order to ascertain the properties of aggregate materials, the contractor shall submit for testing and approval, representative samples of all materials intended for corporation in the works, prior to starting quarry operations, the samples shall be taken by contractor in the presence of the Engineer.

- Tests performed by the contractor shall utilized in assessing the locations, extent of deposits and quantities  of materials  which  will conform to the specifications when properly processed. All testing as carried out by the contractor shall in no way obviate the need for further testing by Engineer.

Approval of specific sources of materials shall not be construed  as final approval and acceptance of materials from such sources.

- Unsatisfactory materials whether in place or not, shall be removed promptly from the site. The contractor shall furnish all necessary material, labor , tools, and equipment and transport required by the engineer for such inspections.

15.4.1.3   Aggregates For Bituminous Paving Mixes

1. Aggregate for use in bituminous, binder and wearing courses,  shall consist of crushed stone.

2. course aggregate shall be the fraction of crushed aggregate material retained on 4.75 mm (No. 4) sieve. Fine aggregate shall be the fraction of crushed aggregate material passing 4.75 mm (N0. 4) sieve. Mineral filler shall be added when the  combined grading of course and fine aggregates is deficient in material passing 0.075 mm(No. 200) sieve.

3. The material from hot bins passing the number 40 sieve (0.425 mm) when tested in accordance with AASHTO T90 shall be non plastic.

4. Aggregate shall not contain gypsum more than 1% and the course fraction of the aggregate shall not contain more than:

5% chert and flint for aggregate to be used in the Wearing course.

5% chert and flint for aggregate to be used in the Binder course.

5. Aggregates shall be of uniform quality, free from decomposed stone, organic matter, shale.

6. The percentage by weight of friable particles, clay lumps, and other deleterious matter shall not exceed 1% as determined by AASHTO T112.

7. Aggregate particles shall be clean, hard, durable and sound. Crushing shall result in a product such that, for particles retained on 4.75 mm (No. 4) sieve, at least 90% by weight shall have 2 or more fractured faces.

8. The flakiness index and the elongation index test should be conducted in accordance with BS 812, the following are the maximum limits:

Wearing Course & Binder Course:

Flakiness Index F.I =  2530

Elongation Index E.I. = 2530

9. Aggregates shall be washed if directed, to remove any clay lumps, organic matter, adherent dust or clay films or other extraneous or deleterious matter that may prevent or detract from proper adhesion of bitumen to the aggregate particles.

10. Material filler shall consist of fine divided mineral matter such as limestone dust if added sperately; hydrated lime; other non-plastic mineral filler, free from clay and organic impurities; or Portland cement, conforming to AASHTO M17.

11. Combined course and fine aggregates for bituminous mixes, including mineral filler, when tested in accordance with AASHTO T27 and T11, shall conform to gradations shown in Table shown below:-

Gradation of Aggregates for Bituminous Mixes

| Sieve Designation | Binder Course | Wearing Course |
| --- | --- | --- |
|  | Percent Passing | Percent Passing |
| 1² (25.0mm) | - | - |
| 3/4² ( 19.0mm) | 100 | 100 |
| 1/2 ² ( 12.5mm) | 829 | 899 |
| 3/8² ( 9.5 mm) | 729 | 829 |
| No. 4 (4.75mm) | 549 | 669 |
| No. 8 (2.36mm) | 419 | 539 |
| No. 20 (1.18mm) | 329 | 419 |
| No. 30 (0.600mm) | 249 | 319 |
| No. 50 ( 0.300mm) | 177 | 218 |
| No. 80 (0.150mm) | 125 | 136 |
| No. 200 ( 0.75mm) | 52 | 4.52.5 |

12. The loss in weight of aggregate after 500 revolutions, when tested in accordance with AASHTO T96, shall not exceed 35%.

Ratio of wear loss =  Abrasionafter100Rev.Abrasionafter500Rev.	is less than or equal 25.

13. When tested for soundness in accordance with AASHTO T104 the course aggregate (retained on No. 4 sieve)  shall not shown sings of disintegration and the loss by weight after 5 cycles shall not exceed 9% in the case of the sodium sulphate test and 12% in the case of the magnesium sulphate test.

14. When tested for resistance to stripping in accordance with the AASHTO T-182 at least 95% coated particles should be achieved. Scandinavian test shall be carried out and at last 60% of the coarse aggregate surfaces area shall remain coated with a bitumen film especially for exposed surfaces other wise anti stripping agent must be added to achieve the required coating.

15. The material shall contain minimum 50% sand equivalent. Test sample shall be taken from hot bins.

15.4.1.4   Heating of Bitumen

1- Heating equipment shall be of an approved type. Any method of heating  that introduces free steam or moisture into the bitumin will not be approved.

2. Bitument shall not be heated more than 170c. materials heated in excess of this temperature will be rejected and shall not be used  in the works.

3. Heating of bitumen shall be uniform and under control at all times, to the specified temperature. The circulation system shall be of adequate size to insure proper and continuous circulation of bitumen during the entire operating  period.

4. Thermometers of adequate range (calibrated in 2 degrees c increments) for accurately measuring the temperature of the bitument, shall be located so as to be readily visible and shall be  kept clean and working order at all times.

15.4.2   BITUMINOUS PRIME AND TACK COATS

15.4.2.1  Scope

This work shall consist of furnishing and applying and MC cutback bitumen prime coat to a previously constructed aggregate base course and applying tack coat on Asphalt or concrete surfaces all as  and where shown on the Drawings.

15.4.2.2   Medium Curing Cutback Bitumen

1. MC-70 cutback bitumen for prime coat shall be used as recommended by ASTM  D2399-83 for open and tight surface, and RC-70 should be used as tack coat.

2. All surfaces to receive either prime or tack coats shall conform with the specified tolerances and compaction requirements and shall be properly cleaned and finally approved before applying any bitumen material.

3. Application of prime and tack coats shall be performed only when the surface to be treated is sufficiently moist and atmospheric temperature is above 15 c. There should be no fog, rain , strong winds, dusty conditions, or dust storms.

4. The surface of all structures shall be protected in an approved manner during the equipment operation. The contractor shall be responsible for making good any staining or damage of the structures to the satisfaction of the Engineer.

5. Traffic shall not be permitted to surfaces after they have been cleaned and prepared for prime coat application.

6. The contractor shall maintain prime or tack coats until it is covered by the subsequent pavement course.

Any area where the coats have been damaged shall be cleaned of all loose material and re-applied at the  contractor's expense.

7. Applying temperature of MC- 70 shall be 45-80c.

8. Areas to be primed shall be including 200 mm widths outside the edge of the permanent line.

9.  Application rate for prime coat shall be 1 lit/sq.m and tack coat application shall be 0.7 lit/sq.m.

10. Asphalt pavement shall not be placed on prime coat before 24 hours, and no traffic is allowed to pass on prime coat.

15.4.3  BITUMINOUS COURSES

15.4.3.1 Scope:

This work shall consist of the general requirements of furnishing materials, mixing at a central mixing plant, spreading and compacting bituminous courses.

15.4.3.2  Job Mix and Project Mixes:

1. The contractor shall submit his proposed Job Mix Formula for approval , at least 30 days prior to beginning production. Therefore , samples from materials use in the preparing mix design ( aggregates and bitumen) shall be sent to specialized laboratories to be tested for final approval of mix design.

2. The Job Mix Formula be established  by the contractor, under the supervision of the Engineer, in the field laboratory Mix design procedures shall conform with the Marshall method of mix design. All trial mixes shall be prepared and tested by the contractor in the presence of the Engineer.

3. The Job Mix Formula shall specify a combination of mineral aggregates including filler and bitumen in such proportions as to produce a Job Mix which is within the limits of the specified gradation and bitumen content ranges and which meets the Marshall test requirements.  It shall also stipulate the mixing temperature at discharge from the mixer which, unless otherwise directed, shall be 170 C.

4. The Marshall test procedure shall be used to determine the percentage of bitumen to be incorporated in the mix. The Job Mix Formula shall take into consideration the absorption of bitumen into the aggregates. Air voids shall be calculated in accordance with the procedure given in the Asphalt Institute Manual, MS-2.

5. When compacting specimens on accordance with the Marshall test procedure, the number of blows applied with the compaction hammer shall be 75 on each test.

6. In order to meet the requirements, an approved additive such as Portland cement, hydrated lime or liquid antistrup agent, may be required in the Job Mix. Portland cement shall meet the requirements of ASTM M 85. Hydrated lime shall meet the requirements of ASTM C207, Type N. Cement or  hydrated lime will normally be required in the approximate range of 2-3% by weight of  the aggregates and shall be added at the cold feed in  dry or slurry form as directed. Liquid antistriping agent, if needed will normally be required in the approximate range of 0.6-1.0% by weight of the bitumen, or according to the manufacturers specifications.

7. Upon receipt of approval of the Job Mix Formula, the Contractor shall adjust his mixing plant to proportion the individual aggregates, mineral filler and bitumen to produce a final project mix within the limits given in Table  shown with respect to the Job Mix gradation:-

Maximum Variations of Project Mix from Approved  Job Mix

| Sieve Designation (squre openings) | Specified Tolerances |
| --- | --- |
| 9.5 mm (3/8 in.) and above |  5.0% |
| 4.75 mm (No. 4) |  4.0% |
| 2.36 mm (No. 8) |  4.0% |
| 1.18 mm (No. 16) |  4.0% |
| 0.600 mm (No. 30) |  4.0% |
| 0.300 mm (No. 50) |  4.0% |
| 0.150 mm (No. 100) |  4.0% |
| 0.75 mm (No. 200) |  1.5% |
| Bitumen Content |  0.3% |
| Temperature of Mix on discharge temperature |  5 C of the specified mixing |

8 Conformance to gradation requirements will be determined on the extracted aggregate in accordance with AASHTO T 30. The bitumen content shall be determined in accordance with AASHTO T 164.

9 The participation of the Engineer in the preparation of the Job Mix Formula shall in no way relieve the Contractor of responsibility for producing project mixes meeting the specified requirements.

10 At the commencement of the contract one copy of the ASTM, AASHTO and Manuals MS-2 MS3, MS and MS22 shall be furnished by the contractor for use by Engineer’s staff.

15.4.3.3   Spreading and Finishing Equipment

1. Bituminous course shall be spread and finished using approved type, self contained, power-propelled pavers of sufficient capacity. Pavers shall be provided with electronically controlled vibratory screed or strike-off assembly and shall be capable of spreading and finishing the course of bituminous mix to the proper thickness and in lane widths applicable to the typical cross sections shown on the Drawings.

2. The pavers shall employ mechanical devices such as equalizing runners, straightedge runners, evener arms or other compensating devices, to maintain trueness of grade and confine the edges of the mix to true lines without the use of stationary side forms. Joint leveling devices shall be provided for smoothing adjusting longitudinal joints between lanes.

3. The paver shall be equipped with receiving hopper having sufficient capacity for a uniform spreading operation. The hopper be equipped with a distribution system to place the mix uniformly in front of the full length of the screed.

4. The screed or strike-off assembly and extensions shall effectively produce a findhed surface of the required evenness and texture without tearing, shoving, or grouging the mix.

5. The paver shall be capable of being operated at forward speeds consistent with satisfactory laying of the mix. Speed shall be fully adjustable

6. The Contractor shall make available, for refference by the Engineer, the manufacturer's instruction and operating manuals for each paver intended for use

15.4.3.4   Surface Preparation.

1. When the bituminous mix is to be placed on a base, course the surface shall be prepared to  meet the appropriate specified compaction and surface tolerance requirements. The surface shall then be primed as specified “Bituminous Prime Coat”. No bituminous mix shall be laid on a prime coat until it has been inspected and approved.

2. Broken, soft, or unstable areas of aggregate base course shall be removed and replaced. The areas shall be excavated to a depth as directed and refilled with the specified bituminous mix.

15.4.3.5   Delivery, Spreading and finishing

A) Delivery of Mix to Site

1. A sufficient number of haul vehicles shall be provided so that adequate supplies of mix are delivered to ensure that continuos paving will be achieved.

2. Hauling equipment for aggregates and bituminous mixes shall consist of vehicles having dump bodies suitable for dumping  materials in a windrow or in spreader boxes. The bodied shall be so constructed  that their volume measurement can be accurately determine. They shall be constructed and maintained such that loss of materials during hauling operations will not occur.

Dump controls shall be capable of operation from the driver’s seat.

3. Hauling equipment for hot bituminous mixes shall have tight, clean, smooth metal beds which are periodically thinly coated with a lime solution or other approved material to prevent adherence of the mix. All hauling units shall be equipped with a canvas or other approved type cover which shall be used to cover the hot material upon loading at the mixing plant and shall not be removed until the mix is discharged into the paver.

4. The dispatching of the hauling vehicles to the site shall be so scheduled  that all material delivered is placed at least 90 minutes before sunset to allow sufficient time for compaction.

Delivery of material shall be at a uniform rate and in an amount well within the capacity of the paving and compacting equipment.

5. The mix at delivery to the paver shall be not more than 10C below discharge temperature at the mixing plant. The minimum temperature for the commencement  of breakdown rolling is 120 C.  Mix loads of temperature less than 120C shall  not be accepted, and the load shall be disposed of and another load used. If there os consistent failure to meet  the temperature requirement the Engineer shall  order paving operations to stop until suitable measures are taken by the Contractor to ensure that temperature requirements are met.

6. Each haul vehicle shall be weight after each loading at the mixing plant and accurate records shall be kept of the gross weight and net weight of each load, for each vehicle dates and time of loading.

B) Setting Out Reference Line

1. The Contractor shall survey the centerline profile and crown of the existing surface or base and determine a reference grade line which will be submitted for approval. A reference line of wire or suitable cord shall be installed at a uniform grade parallel to the approved reference grade line such that conformance with the required geometric, surface tolerance and minimum thickness requirements shall be ensured.

2. The reference line shall be maintained taut and free from sags at all times during spreading and  initial compacting operations.

3. A wire or cord reference line shall be installed on both sides of the paver for the initial bituminous course being laid. Thereafter only one reference line will normally be required, if the paver is equipped with adequate automatic superelevation control.

C) Spreading and Finishing

1. Bituminous mixes shall be laid only when the air temperature is at least 5 degrees C or above  when  the existing surface is free from moisture, and when the weather is not foggy, rainy, dusty or excessively windy (particularly at low temperatures).

2. After completion of surface preparation, the bituminous mix shall be spread and finished true to crown and grade by approved automatically controlled bituminous pavers. The mix may be spread and finished by approved hand methods only where the Engineer determines that machine methods are impracticable. Hand methods include heated hand tampers of at least 10 kg weight and approved type mechanical (vibratory) tampers.

3. The  paver shall spread the bituminous mix without tearing the surface and shall strike a finish that is smooth, true to cross section,  uniform in density and texture and free from hollows, transverse corrugations and other irregularities.

4. The paver shall be operated at a speed which gives the best results for the type of  paver being used and which coordinates satisfactorily with the rate of delivery of the mix to the paver. A uniform rate of placement shall be achieved without repeated intermittent operation of the paver.

5. The mix shall be delivered to the paver in time to permit completion of spreading, finishing and compaction of the mix during daylight hours.

6. If during laying, the paver is repeatedly delayed because of lack of mix or if the paver stands at one location for an extended period, resulting in the (unrolled) mat under and adjacent to the rear of the spreader falling below the minimum temperature for breakdown rolling, the affected portion of mat shall be cut out and discarded and a transverse joint shall be constructed. Paving shall not recommence until the Engineer is satisfied that paving will proceed without interruptions.

7. Contact surfaces of curbing, gutters, manholes, and similar structures shall be painted with a thin, uniform coating of tack coat material. The bituminous mixture shall be placed uniformly high  near the contact surfaces so that after compaction it will be 10 mm above the edge of such structure.

8. If during the paving operations, it is found that the spreading and finishing equipment in operation leaves in the pavement surface tracks or indented areas or other objectionable irregularities that are not satisfactorily corrected by the scheduled operations, the use of the equipment shall be discontinued, until faults are corrected to the approval of the Engineer. If this is not possible, other satisfactory spreading and finishing equipment shall be provided by the Contractor.

9. Transverse joints in succeeding layers shall be offset by at least 2 m. Longitudinal joints shall be offset at least 150 mm.

10. Bituminous mix shall be spread in one or more layers so that, after rolling, the nominal thickness of each layer of  the compacted bituminous material does not exceed 2 to 3 times maximum size of aggregate. This maximum thickness may be increased slightly when such increase is more appropriate to total pavement thickness and provided the Engineer determines that such increased thickness will not be detrimental to the quality of  the finished bituminous course, and the Contractor can show that the required density is attained throughout the layer thickness.

11. Transitions and structure approaches shall  meet the design criteria for geometric, the surface tolerance specifications, and shall not be visually discontinuous or abrupt in appearance.

D) Joints and Edges

1. All joints between old and new pavements or between successive days’ work shall be as to ensure thorough and continuous bond between the old and new material.

2. Before placing fresh mix against previously laid, the contact surface shall be cut back to a near vertical face, and shall be sprayed or painted with a thin uniform coat of tack coat material. Longitudinal joints shall be made by overlapping the paver screed on the previously laid material (cut back as necessary ) and depositing a sufficient amount of fresh mix so that the joint formed will be smooth and tight.

3. Unsupported edges of bituminous layers shall be rolled immediately following the rolling of the longitudinal joint. The material along the unsupported edge may, if approved, be raised slightly by hand methods, to ensure that the full weight of the roller will bear fully on the edge material

4. On completion, the longitudinal edges of bituminous pavement shall be true to the width and alignment as shown on the Drawings. The edges shall be cut back if necessary prior to rolling, additional mix placed manually in a longitudinal strip adjoining each pavement edge, and the edge rolled down to a neat 3:1 (H:V) slope.

5. Transverse joints shall be carefully constructed and thoroughly compacted to provide a smooth riding surface. Joints shall be straight-edged and string-lined to assure smoothness and true alignment

E) Compaction

1. After spreading and strike-off, and as soon as the mix conditions permit the rolling to be performed without excessive shoving or tearing, the mixture shall be thoroughly and uniformly compacted, using approved types, sizes and number of  rollers. rolling shall not be prolonged to the point where cracks appear or shoving or displacement occur.

2. All rollers shall be self-propelled vibratory steel wheel, 2-axle tandem steel-tired and pneumatic-tired types, in proper operating condition, capable of reversing without backlash or tearing of the surface, and shall be operated at numbers of rollers required is 3, of which one must be pneumatic type. The Contractor shall select a suitable method and pattern of rolling that will achieve the required compaction, to Engineers approval.

3. Prior to use on Site of pneumatic-tired rollers, the Contractor shall furnish, for reference and retention by the Engineer, manufacturers’ charts or tabulations showing the contact areas and contact pressures for the full range of tire inflation pressures and for the full range of tire loading for each type and size of compactor tire to be used. The Contractor shall ensure that tire pressures are maintained at all times in conformity with such charts or tabulations. The maximum allowable tolerances shall be plus or minus 35 KN/sq.m (5 psi).

4. Rollers should move at a slow but uniform speed, generally with the drive roll or wheels nearest the paver.

5. Minimum temperature of the mat at which rolling shall be allowed to start is 120c.

6. Breakdown rolling shall be consist of 3 complete coverage unless otherwise directed Rolling shall be longitudinal, and over lapping on successive trips by at least one half the width of the rear wheels.

7. To prevent adhesion of the mix to the rollers, the wheels shall  be kept lightly moistened with water. Excessive use of water will not be permitted.

8. The initial or breakdown rolling shall be followed by intermediate rolling involving 3 coverages with pneumatic-tired rollers unless otherwise specified.

9. Finishing rolling shall  then be carried out by means of tendem power steel rollers unless otherwise designated. If specified density is not achieved, changes shall be made in size and number of rollers being used to ensure the compaction requirements are met.

10. The compacted density shall be equal to or more than 97% and 98% for binder course and wearing course, respectively, of average Marshall bulk specific gravity for each days production unless otherwise directed by the Engineer.

11. Any mix that becomes loose, broken, mixed with foreign material, or which does not conform in all other respects with the specified requirements, shall be removed, replaced with suitable materials and properly finished.

F) Test For Bituminous Pavements

1.  Minimum Tests Required

| Work item | Tests at Source of material | Frequency of tests | Tests at road site | Frequency of tests |
| --- | --- | --- | --- | --- |
| 1- Materials used in Asphalt mix (at Batching plant) | 1- Specific gravity and water absorption 2- Abrasion test 3- Chert content 4- Clay lumps and friable materials 5- Flaky and elongayed particles 6- Soundness | - Test for each source - When materials quality changes - As requested |  |  |
| 2- Materials used in Asphalt mix ( from hot bins) | 1- Gradation 2- Specific gravity and water absorption 3- Plasticity index 4-Sand equivalent 5- Stripping with asphalt | - Test for each source - when materials quality changes - As requested |  |  |
| 3- Asphalt mix design (At batching plant) | 1. Complete mix design in accordance with American Asphalt Institute (MS2) 2. Loss of stability | -For each project -When materials quality changes -When results are not consistent with the mix design results - As requested |  |  |
| 4- Asphalt | At Batching plant 1- Stability 2- Flow 3- Extraction (binder content and gradation) 4- Air voids 5- Voids in mineral aggregates 6- Daily Marshall density | - Test each 3 working days - Test for each batching plant - As requested | Behind spreader 1- Stability 2- Flow 3-Extraction (binder content and gradation 4-Air voids 5- Voids in mineral aggregates 6-Marshall density | -Test each working day - Test for each batch - As requested |
|  | 7-Loss of Stability | - Once a week - As requested | 7- Road density and thickness (after final compaction | - Test each 200 lin.m. per lane - As requested |
|  |  |  | 8-Loss off stability | - Once a week - As requested |

2. The Marshall bulk specific gravity shall be determined in accordance with AASHTO T 166 or AASHTO T 275. The Marshall specimens shall be prepared from the same material used in construction, taken from samples of fresh bituminous mix at  the mixing plant or from trucks delivering mix to the site. Oven heating for up to 30 minutes to maintain the heat of the sample is permissible.

3. The bulk specific gravity of the mix as placed and compacted in situ shall be determined from 100 mm nominal diameter core samples, or slab samples cut from   compacted  layer on the road at locations designated by the Engineer who may require additional tests to determine limits of areas deficient in density, or for recheck.

4. Samples for in situ bulk specific gravity determinations shall be taken in sets of 2 from each pavement location. Minimum frequency of sampling for each bituminous layer shall be one set/lane/500 m, with a minimum of one set per day of placing bituminous layers.

5. The Contractor shall, cut the samples with an approved core drill in the presence of the Engineer. the equipment shall be capable of cutting the mixture without shattering the edges or otherwise disturbing the density of the specimen. The contractor shall fill and compact all test holes at his own expense.

15.4.3.6  Surface Tolerances

1. The fully compacted and completed bituminous course shall conform to the lines, grades and cross sections as shown on the Drawings.

2. The elevations of the finished course shall be checked by the Contractor in the presence of the Engineer at maximum intervals of 25 and at intermediate points as directed.

3. When the finished surface is tested with a 3 m long straightedge, placed parallel to, or at right angles to the centerline, the maximum deviation of the surface from the test edge between any 2 contact points shall not exceed the tolerances specified for each type of bituminous course laid.

4. All areas which exceed the specified tolerances shall be corrected by removing the derective sections of bituminous course and reconstructing them or, if approved, by adding new material and recompacting and finishing to the specified standard or increasing the thickness of the succeeding course.

5. The tolerances specified for evenness of finished surfaces for all types of bituminous course, shall not invalidate the tolerances specified for construction thickness and elevations of such courses.

15.4.3.7   Determination of Thickness of Course

1. Cylinder core samples shall be taken as specified for in situ bulk specified gravity core samples.

2. Thickness of bituminous course shall be determined by average caliper measurement of cores, rounded upwards to the nearest mm.

3. Paved sections to be measured separately shall consist of each 300 lin. m section in each traffic lane. The last section in each traffic lane shall be 300 m plus the fractional part of 300 m remaining. Other areas such as intersections, entrances, etc. Shall be measured as one section and the thickness of each shall be determined separately. Small irregular unit areas may be included as part of another section.

4. One core shall be taken from each section by the Contractor at approved locations and in the presence of the Engineer. When the measurement of the core from any paved section is not deficient by more than 5 mm from the specified thickness, the core will be deemed to be of the specified thickness as shown on the Drawings.

5. When the measurement of the core from any paved section is deficient by more than 5 mm but not more than 20 mm, 2 additional cores spaced at not less than 100 m shall be taken  and used together with  the first core to determine the average thickness of such section.

6. When the measurement of the core from any paved section is less than the specified thickness by more than 20 mm, the average thickness of such section shall be determined by taking additional cores at not less than 5 m intervals parallel to the centerline in each direction from the affected location until, in each direction, a core is taken which is not deficient by more than 20 mm. Exploratory cores for deficient thickness will not be used in average thickness determinations.

7. Any deficiencies in the total thickness of bituminous courses shall be subject to a proportional reduction in the area of (wearing) course measured for payment. Alternatively, the Contractor shall construct all at his own expense, a wearing course overlay, if practicable in the judgement of  the Engineer. Any such overlay  shall be a minimum of 40 mm compacted thickness and to the specified standard  of the course it is overlaying.

8. If the deficiency in total asphalt layers thickness  is from 0 -3 mm, full payment will be made, on condition that deficiencies are not found in more than 10% of the total project. Deficiencies exceeding 3 mm shall be left to the substantial handing -over procedure.

15.4.3.8   Measurement

- Bituminous course shall be measured by squ.m for furnished, paved compacted, tested and approved areas placed according to drawing.

- Any correction, tests, samples, etc. shall not be measured for direct payment.

15.4.4    BITUMINOUS   BINDER AND WEARING COURSES

15.4.4.1 Scope

These works shall consist of furnishing materials, mixing at mixing plant, spreading and compacting bituminous binder and wearing course on an approved aggregate base course as and where shown in the Drawings.

15.4.4.2  Materials:

1. Materials shall conform with relevant requirements of section” Materials” mentioned before.

2. Unless otherwise shown on Drawings, bitumen for binder and wearing course construction shall be 60/70 penetration graded bitumen.

15.4.4.3   job mix and project mix:

1.The Job Mix formula shall be established by the contractor in accordance with the procedure and requirements of section “ Bituminous Course” mentioned before.

2. The Job Mix for bituminous binder and wearing courses shall conform to the following composition limits, as shown in Table:

Job Mix Requirements To Bituminous Courses

| Property Medium-Light |  |  |
| --- | --- | --- |
|  | Binder | Wearing |
| Marshall Stability at 60c (kg) | 800 | 900 |
| Flow (mms) | 2-4 | 2-4 |
| Voids in Mineral aggregate (WA) | 13(-1) | 14(-1) |
| Air Voids (%) | 4-5 | 3-5 |
| Stiffness (kg/mm) |  | 400 (Min) |
| * Loss of stability (%) |  | 25 (Max) |
| Asphalt Content (% in weight) | 4.5-6 | 5-7 |

- This test to be carried out in accordance with AASHTO T 165-82.

- After the Job Mix Formula has been established and approved, all subsequent mixes shall conform to it within the allowable tolerances.

15.4.4.4   Equipment:

Plant and equipment for mixing, hauling, placing and compacting bituminous binder courses and wearing course materials, shall conform with the relevant requirements of section  “ Bituminous Course”.

15.4.4.5   Surface Preparation:

Preparation of surface upon which bituminous binder course and the bituminous wearing course mixes are to be laid, and the use of prime coat, shall be appropriate to type and condition of such surface and shall conform with the relevant requirements of section "Bituminous Courses".

15.4.4.6  Delivery, Spreading And Finishing

A) General :

The delivery, spreading and finishing of bituminous mixes for binder and wearing courses shall conform with the relevant requirements of Section “Bituminous Course”  and  with the following particular requirements.

B) Rollers:

1. Initial  breakdown rolling  shall be carried out by use of 2 dual-drum steel-wheeled rollers each of minimum weight 7,000 kg. These rollers shall be purpose made for compaction of hot bituminous courses.

2. Intermediate rolling shall be carried out by of at least 2 self-propelled, tandem pneumatic smooth-tired rollers each capable of exerting contact pressures of up to 690 kN/sq.m (100 psi) and ballast- adjustable to ensure uniform wheel loading.

3. Final rolling shall be carried out by use 2, 2-axle tandem, steel-tired  rollers each of minimum weight 10.000 kg, capable of exerting contract pressures of up to 65 kg/cm (350 Ib/in.)

C) Standard of Compaction:

The  compacted density of  the bituminous wearing course shall be not less than 98% of the average Marshall bulk density for each day’s production.

15.4.4.7  Sampling And Testing

Sampling and testing shall conform with the relevant requirements of  Section “Bituminous Course “.

15.4.4.8   Surface Tolerances

1. Surface tolerances shall conform with the relevant requirements of  Section “Bituminous Course “, and with the following particular requirements.

2. The tolerances on elevations of the final bituminous wearing course surface shall not be greater than 10 mm.

3. When the finished wearing course surface is tested with a 3 m long straightedge, placed parallel to, or at right angles to the centerline, the maximum deviation of the surface from the testing edge between any 2 contact points shall not exceed 5.0 mm.

15.4.4.9   Determination of Thickness

1. Procedures for determining the average compacted thickness of bituminous binder and wearing course shall conform with the relevant requirements of Section ” Bituminous Courses” and the following particular requirements.

2. Cores for thickness measurements of binder course shall be used  to determine if changes are necessary  in the constructed thickness of the wearing course and thickness deficiencies in the binder course.

15.4.4.10   Measurement

1. Bituminous binder course and bituminous wearing course shall be measured by sq.m. of mix finished, spreaded, compacted, completed and accepted.

Measurements shall be of the areas and thickness as shown on the drawings.

2. Deficiencies in thickness of wearing course shall, unless an overlay is constructed at contractor's expense, result in proportion only of  the wearing course area being measured for payment. Proportions shall be determined in accordance with the thickness deficiencies and area proportions  mentioned in section " Bituminous Course".

3. Bituminous Prime coat and Tack coat shall be measured as prescribed in "Bituminous Prime and Tack Coats".

4. All other items shall not be measured for direct payment as prescribed in  section " Bituminous Course".

15.4.5   SIGNING:

15.4.5.1  SCOPE:

1.	These works shall consist of furnishing and installing  road signs, post 	assemblies, including all sign panel lettering as Engineer requirements.

2.	All signs shall be lettered in both Arabic and English.

15.4.5.2  MATERALS:

1-Concrete

Concrete for reinforced concrete footing shall be B200, Un-reiforced 	concrete to support single signs shall be B150.

2-Sign Supports:

Steel for sign supports shall conform to ASTM A53, Grade B

4-Galvanization:

All steel supports shall be galvanized in conformity with ASTM A123. All bolts, nuts, and washers shall be galvanized  in conformity with ASTM  153.

5-Sign Materials:

1.	Aluminum alloy panels, sheets and miscellaneous hardware shall conform with ASTM B 209, or B 221, as appropriate. All aluminum alloys shall have a minimum tensile strength of 2,500 kg/sq.cm and a minimum yield strength of 2,000 kg/sq.cm.

2.	Extruded aluminum panels shall have a minimum thickness of 2.7 mm.

Panels shall normally by 30 cm nominal width, except  when smaller widths are necessary to size  given sign correctly.

3.	Sheets for plain aluminum signs shall have a minimum thickness of 3 mm unless otherwise specified.

6-Reflective Sheeting

1.	Reflective sheeting shall be of the " Engineering Grade"  type unless otherwise  specified.

2.	Reflective sheeting shall consist of synthetic sheet resin or other approved noncellulostic materials, transparent plastic of the colors specified, and a retro-reflective system (i.e. glass spheres). These spheres shall adhere to the synthetic sheet resin and be embedded beneath a flexible transparent plastic film forming a smooth flat surface.

3-	The reflective sheeting shall have a precoated pressure sensitive adhesive backing. The sheeting shall adhere tightly to the prescribed surfaces when applied in accordance with the manufacturer’s recommendations.

4-	The precoated adhesive shall have no staining effect on the reflective sheeting and shall be mildew resistant. The protective liner for preventing contamination or premature adhesion shall be removable by peeling without the necessity of soaking in water or other solvents.

5-	The Contractor shall submit samples of each color of reflective sheeting for approval. Unless otherwise specified, flat angle "scotchlite" type colors shall be used for all sign face lettering, symbols  and borders. Colors shall conform to International Road Sign colors.

6-	The Reflective Sheeting shall meet the requirements and satisfy the tests as laid down in the US Federal Specification  L-5-300B.

15.4.5.3  Construction and Installation

Sign Faces

1-	The type, color design and size of all sign faces shall be as shown on the Drawings, or shall meet the standards adopted in the "European Rules concerning road traffic, signs and signals" agreed at the 1968 Vienna Convention and subsequent supplementary provisions in the 1971 Geneva Agreements.

2-	The Contractor shall prepare and submit for approval, 3 sets of detailed working drawings for the sign faces, in respect of all required danger, warning, regulatory and informative signs. Complete details of arrangement and spacing for Arabic, English lettering, and mounting hole locations, shall be shown on these drawings.

3-	Mounting hole spacing for screws, bolts or rivets shall not exceed 200 mm. Characters shall be secured to the sign using non-twist, corrosion resistant screws, bolts or rivets.

4-	The correct Arabic (and English) spelling of the official names of towns, disstricts, roads and streets etc., will be supplied by the Engineer. Sizes and style of lettering and arrows shall be as shown on the Drawings or as established by the Engineer. Arabic shall be in "Naskh" characters. Sign messages for each direction sign shall be either as indicated on the Drawings or as otherwise directed. Where English lettering is shown, the lateral extent of Arabic and English lettering for each message shall coincide.

5-	The rear sign face of all signs shall be painted with 2 coats of priming paint pigmented with chromates or chromes (excluding lead chromes) plus 2 coats of weather-resiting dull silver gray paint. Where connection of large aluminum sheet signs to a steel stiffening frame is required, the studs or screws, bolts and washers shall be painted on the sign face to properly match the color of the surrounding material.

6-	Signs delivered to the site shall be stored off the ground and under cover in an approved manner. Any sign damage, discolored, or defaced during transportation storage, or erection will be rejected and shall be replaced at  the Contractor's expense.

Footings

1.	Post footings shall be excavated to the dimensions shown on the Drawings. Footings shall be installed and backfilled flush with the finished ground surface. Class B200 concrete shall be placed against the undisturbed excavated faces, except that the top 150 mm of each footing shall be formed.

Concrete shall be thoroughly rodded and spaded to minimize voids. Tops of  footings shall be finished with a wood float and all exposed edges shall be rounded with an edger.

2.	Backfill, where needed, shall be thoroughly compacted using mechanical tampers. Care shall be taken to prevent damage to the finished concrete. Backfill shall be brorght up to finished ground level.

3.	Pipes or posts to be set in concrete bases shall be firmly supported with the correct orientation and plumbed vertical before any concrete is placed. Posts or pipes that are found to be out of plump after installation will not be accepted and shall be replaced at the Contractor's expense.

Sign Posts and Support Assemblies

1.	Signs shall normally be erected so that the edge and face of the sign are truly vertical and the face is at an angle of 87 degrees to the centerline, i.e. facing slightly towards the centerline of the traffic lanes which the sign serves. Where lanes divide or are on sharp horizontal curves, the Contractor shall orient sign faces as required by the Engineer, so they will be most effective and so as to avoid specular reflection and glare.

2.	The Engineer will establish the longitudinal location of each sign which shall be laterally positioned from the shoulder or curb as shown on the Drawings. The Contractor shall  establish the location of the sign supports and shall be responsible for the proper elecation, off-set, and orientation of all signs. If any stakes are lost, damaged, displaced, or removed, the Contractor shall have them reset at his own expense.

3.	Post lengths shown on the Drawings for small signs are approximate only. The Contractor shall be responsible for determination of post lengths to provide the required vertical clearance. Field cutting of posts shall be performed by sawing off the bottom end.

4.	Sign Supports shall be fabricated as detailed on the Drawings. When galvanizing is specified, assemblies shall be hot-dip galvanized after fabrication. All welds shall be mechanically cleaned before galvanizing.

Galvanizing materials on which the galvanizing has been damaged in transporting, handling, or erection will be rejected or may, with the approval of the Engineer, be repaired in the field by the zinc alloy stick method.

Required field welds and adjacent areas on which galvanizing has been damaged shall also be galvanized by this method.

5.	The contractor shall submit 3 copies of the fabricators certificates stating that the materials supplied conforms with all of the specified requirements.

Fastening Signs to Posts

1-	Sign panels larger than 1 sq.m in area shall be supported on 2 or more posts as shown on the Drawings.

2-	Signs shall be fastened to sign supports in accordance with the recommendations of the sign manufacturer and to the satisfaction of the Engineer.

3-	All bolt heads, screw heads, and washers used to install signs on support shall be such that they do not protrude from the surface of the signs.

The heads of bolts or screw shall be as nearly as practicable the same color as the background or message area at the point where the hardware is exposed.

4-	Fastener systems shall as far as practicable be designed so not to require the drilling of the sign face.

5-	When steel signs are mounted with aluminum hardware or where aluminum signs are mounted with steel hardware or on steel posts, approved asphalt, nylon or neoprene insulation shall be installed at all points where dissimilar metals may  come into contract.

15.4.5.4 Measurement

1. Signs shall be measured by the number including all relevant works, excavation, backfilling, concrete, reinforcement and other ancillary items shall not be measured for direct payment, but shall be considered as subsidiary works, the costs of which will be deemed to be included.

15.4.6    PAVEMENT MARKINGS FOR TRAFFIC

15.4.6.1  Scope:

1. These Works shall consist of the furnishing and application, of the traffic markings and to highway pavements for the guidance, control and safety of vehicular and pedestrian traffic.

2. White (Class A) and yellow  (Class B) painted markings shall include centerlines, lane lines, border (edge) lines, pedestrian crossing lines, stop lines, directional arrows, lettering and symbols using the following materials as appropriate and as on the Drawings.

15.4.6.2   Paint And Thermoplastic Materials

Reflectorized Paint (RP)

1. RP shall consist of a mixture of binder, white or yellow pigment and  filler specifically compounded for cold application and  adhesion to finished  paved areas. Paint shall be reflectorized by adding reflective spheres before adhesion the film dries or sets.

2. White and yellow RP shall conform to AASHTO M248 Type III. The surface application  glass spheres shall conform to AASHTO M247, Type I.

15.4.6.3   Application :

A) Equipment for Pavement Marking

1. The equipment used for pavement marking shall consist of approved types of truck-mounted units, or motorized equipment, or manually operated equipment, depending on the type of marking required. The truck-mounted or motorized unit for centerlines, lines, and edge lines shall consist of a mobile, self-contained unit carrying its own material and capable of operating at a maximum speed of 10 km/h while applying paint. The  hand applicator equipment shall be sufficiently to install centerlines, lane lines, edge lines gore striping,trun lines, crosswalks, stop lines, arrows, and legends

2. Spraying equipment shall be capable of satisfactorily applying the paint under pressure with a uniformity of feed through nozzles spraying directly on the pavement. Each paint tank shall be equipped with cut-off valves which will enable broken (skip) lines to be sprayed automatically. Each nozzle shall have a mechanical bed dispenser that will operate simultaneously with the spray mozzle and distribute the beads in a uniform pattern at the rate specified. Each nozzle shall also be equipped with suitable line guides and shall provide a method for cleaning the surface of dust just prior to paint application.

3. The spray machine for application of reflectorized paint lines and other markings shall have an attachment to accurately regulate the rate of application and a tachometer or other approved device to ensure uniform paint application at the designated rate. It shall be adjustable to enable the painting of 1 or 2 adjacent lines simultaneously along the centerline. The paint shall be properly agitated while in operation .

4. An automatic glass sphere dispenser with synchronized automatic cut-off shall be attached to the applicator machine. The dispenser shall utilize pressure type spray guns which will embed the spheres into the surface to at least 0.5 times the sphere diameter. The dispenser shall also be equipped with an automatic cut-off synchronized with the cut-off   of the thermoplastic material.

5. Hand equipment shall be used only for painted markings, including arrows, crosswalks, stop lines, symbols and legends, and it shall hold a minimum of 25kg and not more than 100kg of molten material unless otherwise agreed between the Engineer and the contractor.

B) Setting Out and Pavement Preparation

1. The Contractor shall set out all control points necessary for locating paint lines and markings. On irregular widths of  roads, the locations of boarder (edge) lines shall be adjusted so as to fall continuously on the pavement.

The locations of all painted markings shall be accurately established and shall be subject to approval before application  commences. Markers shall not be located over longitudinal or transverse pavement joints.

2 The area of road surface on which marking is to take place shall be free of dirt, grease, oil, moisture, losse or unsound layers, and any other material which could adversely affect the bond. The areas shall be thououghly cleaned to the satisfaction of the Engineer before proceeding with painting.

3. Pavement marking shall not proceed when there is moisture on the pavement surface or the air is moisty; or the surface temperature of the pavement is below 10 degrees C; or when wind or other conditions may cause a film of dust to be deposited on the surface, or in other conditions that, in the opinion of the Engineer, could displace, damage, or adversely affect the bonding of the material to the pavement surface. Any markings damaged due to water or rain within 20 minutes after application, shall be removed and replaced at the Contractor's expense.

C) Painting and Adhesive Film Application

1. The use of Class A (white) paint or Class B (yellow) paint and the type of paint material shall be in accordance  with the design standards and as shown on the Drawings.

2. Application of the various categories of point to the pavement surface shall be carried out in accordance with the equipment manufacturer's recommendations and as shown on the drawings and directed by the Engineer.

3. Painting applications may include centerlines, border (edge) lines, 'no passing' lines, intersection markings chevron striping (in groe areas), pedestrian crossings, letters, arrow, symbols and other special purpose pavement markings.

4. Preformed reflectorized thermoplastic film shall be utilized only where specified for markings such as intersection markings, lettering,arrows, symbols and other special purpose markings. Application shall be in accordance with the manufacturer's recommendations and shall be carried out in the presence of the Engineer.

D) Reflectorized Paint (RP) Application

1. Traffic paint shall be throroughly mixed in the shipping container before placing in the machine tank. The paint machine tanks, connections, and spray nozzles shall be thoroughly cleaned each day with thinner before starting any spraying.

2.The minimum wet film thickness for all painted areas shall be 0.4 mm.

The minimum rate of application for 100 mm width paint lines shall be as follows:

a- Continuous (soild) paint lines: 40 ltr/km for smooth surfaces and 50 ltr/km for rough surfaces.

b- Broken (skip) paint lines: 14 ltr/km for smooth surfaces and 17.5ltr/km for rough surfaces (assuming gap length is double the length of paint line).

Rates shall be modified proportionately for other widths of trarffic lines.

3. The measrued application rate shall not vary from the approved rate by more than 5% in any 1/km. At any point where a check indicates a variation in excees of 5% painting shall be stopped and the equipment adjusted or replaced. Identifiable areas of deficiency shall be corrected as directed.

4. Immediately following the application of paint, a uniform application of glass beads shall be applied at the rate of 0.6-0.7 kg/ltr of paint.

E) Protection of Markings

1. Immediately following the application of paint lines and other markings on pavement open to traffic, traffic cones and other devices shall be placed alongside or over the paint at intervals not exceeding 10 m and shall remain on place until the paint has dried.

2. Traffic shall be prevented from crossing wet paint lines and the Contractor shall  use sufficient numbers of flaymen, barricades, or  other protection, particularly at crossings to prevent traffic from crossing wet paint. Section of paint which have been damaged by traffic before the paint has cured, shall be repaired and pavement outside the painted area cleaned at the contractor's expence.

15.4.6.4  Sampling and Testing

1. All material shall be shipped to the job site in undamaged, sealed, original packaging clearly identifying each material as to name, color, manufacturer, batch number, and date of manufacture. All material shall be accompanied by certified test results verifying compliance with all specified physical and chemical requirements.

2. All paint products and other materials designated by the Engineer shall be sampled for testing. Sampling shall be performed by the Contractor in the presence of the Engineer. Materials shall be sampled in their original containers. All samples shall be packaged for shipment as approved by the Engineer. Samples shall be transported to the mobile field laboratory or to an approved independent laborory, as directed by the Engineer. Paint materials shall  not be used until aproved by the Employer.

15.4.6.5   Measurement

Painted Pavement Lines and Painted Pavement Markings shall be deemed to be included in the price of the painted surfaces.

15.4.7    CONCRETE CURBS AND SIDEWALKS

15.4.7.1 Scope

These work shall consist of furnishing and constructing concrete curbs and concrete paving to sidewalks as and where shown in the Drawings.

15.4.7.2   Materials and Precast Manufacture

A)  Concrete

Portland cement concrete shall be class 250 for all in situ and precast concrete except base course and backing concrete which shall be 200

B) Mortar

Mortar shall consist of cement and fine aggregate having the same proportions used in the concrete construction.

C) Precast Concrete Units

1. All precast units shall be manufactured to the dimension shown on the Drawings Manufacturing tolerances shall be 3mm in any one dimension.  End and edge faces shall be perpendicular to the base. Each precast curb unit shall normally be 0.5m in length and this length shall be reduced to 0.25m or as directed  where units are to be installed along curves of less than 10m radius.

2. For horizontal curves of radius less than 10m, curb units shall be manufactured to the radius shown and in such circumstances where straight elements or portions of straight elements shall not be used.

3. Precast concrete tiles (paving slabs) shall be 300x300mm by 35 mm thickness with 5mm edge level.  The tile face shall be grooved in squares of size agreed by the engineer as appropriate to the tile dimensions coloring of the top layer, where required shall be achieved using mineral oxides.

4. Precast units shall be cast  upside down in approved steel molds under conditions of controlled temperature and humidity.  The Engineers approval of the samples will not be considered final and the Engineer may reject any precast units delivered to the site which do not meet the required standards.

15.4.7.3   Precast Concrete Curbs

1. The subgrade shall be excavated to the dimensions as shown in the drawings, and the surface of subgrade shall be leveled and compacted to at least 95% AASHTO T180 maximum density.

2. Forms for the concrete base shall be approved wood or steel. All forms shall be sufficiently strong and rigid and securely staked and braced to obtain a finished product correct to the dimensions, lines and grade required. Forms shall be cleaned and oiled before each use . If approved, forms for the concrete base may be omitted and the concrete placed directly against undisturbed excavated faces.

3. Base course concrete shall be placed, compacted and shaped to the sections shown on the Drawings. Concrete shall be compacted with an approved internal  type vibrator or if approved, by hand spudding and tamping.

Edge shall be rounded if necessary by the use of wood molding or by the use of an edger as applicable. The concrete base shall be finished to a true and even surface with a wood float. Concrete shall be membrane or water cured for at least 7 days before precast units are placed thereon.

4. Precast units shall be soaked in water immediately before installation.

Units shall be set accurately in position in mortar on the concrete base. Joints between precast units shall not be mortared unless otherwise shown on the Drawings. Units shall be closely spaced and every 10 m run shall be provided with an expansion joint.

5. Where curbs or gutters are installed on existing concrete pavement and using epoxy resin adhesive, the installation procedures shall conform with those specified for raised pavement markers in Section "Pavement Markings for Traffic".

6. After curbs have been installed, steel forms shall be erected and concrete backing, shall be placed as shown on the Drawings.

Pavement courses shall not be laid against curbs until the concrete backing has membrane or water cured for at least 14 days.

7. The tolerances on alignment of completed precast shall be as specified for in situ concrete construction.

8. The area adjacent to completed and accepted curbs shall be backfilled with approved material to the top edges of the curbs to 95 % AASHTO T180 maximum density.

#### 15.4.7.4  Precast Concrete Tiles  (Paving Slabs)

1. Excavation and the placing of bedding material shall be as specified for in situ concrete paving. The surface of the completed bedding shall be dampened sand base course concrete shall be placed and finished to the thickness 40 mm minimum thickness.

2. The base course concrete shall be cured by water or membrane cured as specified for in situ concrete paving, for not less than 7 days before placing precast tiles.

3. Concrete tiles shall conform to the requirements of JSS/45/1977.

4. Immediately prior to tile laying,  the concrete base course shall be dampened and the  on concrete tiles shall be immersed in water.  Tiles shall then be laid true to line and grade on a 10 mm to 20 mm thickness of mortar joints shall be 3 mm wide.

5. The tolerance on smoothness of precast concrete tiled areas and removal and replacement of defective tiling, shall be as specified for in situ concrete paving .

6. Tiles shall be cleaned 24 to 36 hours after laying and joints shall be mortared using, if approved, a plasticizer in the mortar to improve workability and to enable the mortar to be readily smoothed and finished.  As soon as the mortar has partially set, all mortar material shall be raked from the top 3 mm depth of the joint, using a grooving tool to produce a smooth circular section.

7. When the mortar is sufficiently set, the surface shall be sprinkled with water and covered with plastic or nylon sheets during the curing period.  The sheets shall be left in place until final hardening of the mortar, or as directed.  All foreign material, wood, concrete, mortar lumps, etc., shall then be removed and the surface cleaned of staining, discoloration and other blemishes.

8. In cases where tiles  are required to be  cut at the boundaries of tiled areas,   due to the presence of obstacles,  poles, hydrants, etc.,   or in the   construction of the driveways or side roads, the contractor shall cut the tiles or substitute in situ concrete of at least the same quality as the tile concrete.  The Engineer will decide, after trials,  on the method to be adopted.  Cutting of tiles or substitution of in situ concrete shall be kept to a minimum.  The contractor shall complete the areas using uncut precast tiles to the maximum extent practicable.

9. Where a side walk crosses the entrance to a shop or a house, etc., which is higher than the side walk, the contractor shall construct steps,  formed  by a curb and a complete or partial tile.  Steps shall be backfilled with concrete of the same quality as specified for concrete base course.

10. Steps shall be constructed wherever the difference in elevation between the entrance and the side walk is more than 250 mm.  The contractor shall submit for approval, prior to commencing any sidewalk construction,  a list of locations where steps will be required, together with design details for their construction.

11. In situ concrete paving and precast concrete tiling shall be measured by sq.m furnished, constructed or installed, completed,  and accepted .  Measurements shall be of the surface area and no deduction shall be made for minor obstructions such as manholes, poles or similar small unpaved or untilled areas

12. Concrete Tiled steps shall be measured by sq.m furnished, constructed or installed,  completed, and accepted.  Measurements shall be of the horizontal projection of the steps.

13. Excavation, backfilling, bedding, concrete base course, concrete backing,  construction in and around obstacles, poles , manholes, flower beds, cutting and shaping of tiles on curves,  jointing , and finishing as walls and fences , etc. shall not be measured for direct payment, but shall be considered as subsidiary works, small the costs of which will be deemed to be included in the contract prices  for the pay items.

# 16.EQUIVALENT STANDARDS

The gollowing nominal equivalents are used throughout this specification:

1 Kilogram = 2.205Ibs

  - Centimeters = 1

Aggregate gradings

aggregate Gradings given throughout this Specification are based on the following tables of sieve sizes:

| Size of Mesh |  |
| --- | --- |
| Inches | Approximate Millimetres |
| 3 | 76 |
| 2 ½ | 64 |
| 2 | 51 |
| 1 ½ | 38 |
| 1 | 25 |
| ¾ | 19 |
| ½ | 13 |
| 3/8 | 10 |
| 3/16 | 5 |
| 1/8 | 3 |

| B.S. Test sieves |  |  |
| --- | --- | --- |
| Sieve No. | Inches | Approximate Millimeters |
| 7 | 0.095 | 2.4 |
| 14 | 0.047 | 1.2 |
| 25 | 0024 | 0.3 |
| 52 | 0.012 | 0.3 |
| 100 | 0.006 | 0.15 |
| 200 | 0.003 | 0.076 |

Standard weights of mild sheet rounds

| British Sizes |  |  | Metric sizes |  |
| --- | --- | --- | --- | --- |
| Diameter in inches | Approximate diameter in millimeters | Weight in kilograms per meter run | Diameter in millimeters | Weight in kilograms per meter run |
| 3/16 | 4.76 | 0.14 |  |  |
|  | 17.46 |  | 5 | 0.15 |
|  |  |  | 6 | 0.22 |
| ¼ | 6.35 | 0.25 |  |  |
|  |  |  | 7 | 0.30 |
| 5/16 | 7.94 | 0.39 |  |  |
|  |  |  | 8 | 0.39 |
| 3/8 | 9.52 | 0.56 |  |  |
|  |  |  | 10 | 0.62 |
| 7/16 | 11.11 | 0.76 |  |  |
|  |  |  | 12 | 0.89 |
| ½ | 12.70 | 0.99 |  |  |
|  |  |  | 14 | 1.21 |
| 9/16 | 14.29 | 1.26 |  |  |
| 5/8 | 15.87 | 1.55 |  |  |
|  |  |  | 16 | 1.58 |
| 11/16 | 4.76 | 1.88 |  |  |
|  |  |  | 18 | 2.00 |
| ¾ | 19.05 | 2.24 |  |  |
|  |  |  | 20 | 2.47 |
| 13/16 | 20.64 | 2.63 |  |  |
|  |  |  | 22 | 2.98 |
| 7/8 | 22.22 | 3.04 |  |  |
| 15/16 | 23.81 | 3.49 |  |  |
|  |  |  | 24 | 3.55 |
| 0.1 | 25.40 | 3.98 |  |  |
|  |  |  | 26 | 4.17 |
|  |  |  | 28 | 4.83 |
| 1-1/8 | 28.57 | 5.03 |  |  |
|  |  |  | 30 | 5.50 |
| 1 ¼ | 31.75 | 6.21 |  |  |
|  |  |  | 32 | 6.31 |
|  |  |  | 34 | 7.13 |
| 1 3/8 | 34.92 | 7.52 |  |  |
|  |  |  | 36 | 7.99 |
|  |  |  | 38 | 8.90 |
| 1 ½ | 38.10 | 8.95 |  |  |
|  |  |  | 40 | 9.87 |
| 1-5/8 | 41.27 | 10.50 |  |  |
| 1 ¾ | 44.45 | 12.18 |  |  |
|  |  |  | 45 | 12.48 |
| 1-7/8 | 47.62 | 13.98 |  |  |
|  |  |  | 50 | 15.51 |
| 2 | 50.80 | 15.91 |  |  |

| ###### Pipes |  |
| --- | --- |
| Diameter inches | Approximate millimeters |
| ½ | 13 |
| ¾ | 19 |
| 1 | 25 |
| 1 ¼ | 32 |
| 1 ½ | 38 |
| 2 | 51 |
| Diameter inches | Approximate centimeters |
| 3 | 8 |
| 4 | 10 |
| 6 | 15 |
| 9 | 23 |
| 12 | 30 |

| ###### Standard wire Gauge |  |  |
| --- | --- | --- |
| S.W.G. Number | Approximate thickness |  |
|  | Millimeters | inches |
| 9 ½ | 3.9 | 0.152 |
| 10 | 3.3 | 0.128 |
| 10 ½ | 3.1 | 0.122 |
| 12 | 2.6 | 0.104 |
| 16 | 1.6 | 0.064 |
| 22 | 0.7 | 0.028 |
| 24 | 0.6 | 0.022 |
| 27 | 0.4 | 0.016 |

| ##### Wall thick |  |
| --- | --- |
| Blockwork |  |
| nominal |  |
| Cm | Inches |
| 10 | 4 |
| 15 | 6 |
| 20 | 8 |
| 25 | 10 |
| 30 | 12 |
| 35 | 14 |
| 40 | 16 |
| 45 | 18 |
| 50 | 20 |

General mixing tables for concrete

| ###### Quantities of materials required for mixing in batches |  |  |  |
| --- | --- | --- | --- |
| Nominal mix | Cement Kilos | Aggregates |  |
|  |  | Fine cube meter | Coarse cube meter |
| E | 176 | 0.50 | 1.00 |
| D | 240 | 0.50 | 1.00 |
| C | 282 | 0.50 | 1.00 |
| B | 361 | 0.50 | 1.00 |
| A | 488 | 0.50 | 1.00 |

| Approximate quantities of materials required to make one cubic meter |  |  |  |
| --- | --- | --- | --- |
| Nominal mix | Cement kilos | Aggregate |  |
|  |  | Fine cube meter | Coarse cube meter |
| E | 158 | 0.45 | 0.90 |
| D | 214 | 0.45 | 0.89 |
| C | 245 | 0.44 | 0.87 |
| B | 303 | 0.42 | 0.84 |
| A | 390 | 0.40 | 0.80 |

| ###### Quantities of materials required for mixing with one bag of cement |  |  |  |
| --- | --- | --- | --- |
| Nominal mix | Cement Bags of 1 cwt. Or 50 kg. | Aggregate |  |
|  |  | Fine cube meter | Coarse cube meter |
| E | 1 | 0.14 | 0.29 |
| D | 1 | 0.10 | 0.21 |
| C | 1 | 0.09 | 0.18 |
| B | 1 | 0.05 | 0.14 |
| A | 1 | 0.05 | 0.10 |

MECHANICAL WORKS

MAIN   INDEX

| ITEM | TITLE | Section | Page number |
| --- | --- | --- | --- |
| 0 | Reference Publication | Sec0 (1 – 20) | 206 |
| 1 | General Conditions and Requirements for Mechanical Works | Sec1 (1 – 8) | 231 |
| 2 | Thermal Insulation for Mechanical Systems | Sec2 (1 – 21) | 242 |
| 3 | Mechanical Sound and Vibration Control | Sec3 (1 – 10) | 272 |
| 4 | Low Pressure Duct Work | Sec4 (1 – 8) | 285 |
| 5 | Dirty Exhaust and Special Extract Systems | Sec5(1 – 11) | 296 |
| 6 | Air Conditioning Equipment | Sec6 (1 – 5) | 310 |
| 7 | Air Terminals; Diffusers, Registers and Grills | Sec7 (1 – 3) | 318 |
| 8 | Fire Protection Systems | Sec8 (1 – 7) | 322 |
| 9 | Fire Pumps | Sec9 (1–11) | 331 |
| 10 | Medical Gas and Vacuum Piping | Sec10 (1–17) | 346 |
| 11 | Equipment | Sec11 (1– 13) | 366 |
| 12 | Demotic Cold and Hot Water Services | Sec12(1– 15) | 372 |
| 13 | Drainage, Above Ground | Sec13 (1 – 4) | 391 |
| 14 | Drainage, Below Ground | Sec14 (1 – 9) | 395 |
| 15 | Plumbing, Fixtures | Sec15 (1 – 7) | 406 |
| 16 | Testing & Commissioning Specifications | Sec16 (1– 25) | 415 |

SECTION:  0.00

# REFERENCE PUBLICATIONS

## PART 1   GENERAL

1.1   	REFERENCES

Various publications are referenced in other sections of the specifications to establish requirements for the work. These references are referred to in the text of relevant sections by basic designation only. In this section those references are indicated by document number, date and title. The document number used in the citation is the number assigned by the sponsoring organization. However, when the sponsoring organization has not assigned a number to a document, an identifying number has been assigned for reference purposes.

AMERICAN ASSOCIATION OF STATE HIGHWAY & TRANSPORTATION OFFICIALS (AASHTO)

AASHTO HB-16		(1996) Standard Specifications for Highway Bridges

AMERICAN BEARING MANUFACTURERS ASSOCIATION (ABMA)

ABMA 9			(1990) Load Ratings and Fatigue Life for Ball Bearings

ABMA 11 		(1990) Load Ratings and Fatigue Life for Roller Bearings

AMERICAN INSTITUTE OF STEEL CONSTRUCTION (AISC)

AISC M015L	(1991) Manual of Steel Construction Load & Resistance Factor Design

AISC S328	(1986) Specification for Structural Steel Buildings Load & Resistance Factor Design

AISC S342L	(1993) Load and Resistance Factor Design Specification for Structural Steel Buildings

AIR MOVEMENT AND CONTROL ASSOCIATION (AMCA)

AMCA 99		(1986) Standards Handbook

AMCA 99-0401-66	Classification for Spark Resistant Construction

AMCA 201		(1990) Fan Application Manual - Fans and Systems

AMCA 210		(1990) Testing Fans for Rating

AMCA 211		(1987) Certified Ratings Program for Air Moving Devices

AMCA 220		(1982) Air Curtain Units

AMCA 261		(1992) Directory of Products Licensed to Use the AMCA Seal

AMCA 300	(1985; R 1987) Reverberant Room Method for Sound Testing of Fans

AMCA 301	(1990) Calculating Fan Sound Ratings from Laboratory Test Data

AMERICAN NATIONAL STANDARDS INSTITUTE (ANSI)

ANSI A13.1		(1996) Scheme for the Identification of Piping Systems

ANSI B16.18		(1984; R 1994) Cast Copper Alloy Solder Joint Pressure Fittings

ANSI IP-20	(1988) Drives Using Classical V-Belts & Sheaves Cross Sections, A, B, C, and D

ANSI IP-22		(1991) Drives Using Narrow V-Belts and Sheaves

ANSI S1.4		(1983; R 1994) Sound Level Meters

ANSI Z21.22	(1999) Relief Valves & Automatic Gas Shutoff Devices for Hot Water Supply Systems

AMERICAN PETROLEUM INSTITUTE (API)

API RP 1110		(1997) Pressure Testing of Liquid Petroleum Pipelines

API RP 1631		(1997) Interior Lining of Underground Storage Tanks

API Spec 6D	(1994; Supple 1 June 1996; Supple 2 Dec 1997) Pipeline Valves (Gate, Plug, Ball, and Check Valves)

API Spec 6FA		(1999) Fire Test for Valves

AMERICAN SOCIETY OF HEATING, REFRIGERATING AND AIR-CONDITIONING ENGINEERS (ASHRAE)

ASHRAE 52.1	(1992) Air-Cleaning Devices Used in General Ventilation for Removing Particulate Matter

ASHRAE 68		(1986) In-Duct Sound Power Measurement Procedure for Fans

ASME INTERNATIONAL (ASME)

ASME B1.1		(1989) Unified Inch Screw Threads (UN and UNR Thread Form)

ASME B16.1		(1998) Cast Iron Pipe Flanges and Flanged Fittings

ASME B16.3		(1998) Malleable Iron Threaded Fittings

ASME B16.4		(1998) Cast Iron Threaded Fittings

ASME B16.9		(1993) Factory-Made Wrought Steel Butt welding Fittings

ASME B16.21		(1992) Nonmetallic Flat Gaskets for Pipe Flanges

ASME B16.22	(1995; B16.22a1998) Wrought Copper & Copper Alloy Solder Joint Pressure Fittings

ASME B18.2.1	(1996) Square and Hex Bolts and Screws (Inch Series)

ASME B18.2.2	(1987; R 1993) Square and Hex Nuts (Inch Series)

ASME B1.20.1	(1983; R 1992) Pipe Threads, General Purpose (Inch)

ASME B16.5		(1996) Pipe Flanges and Flanged Fittings nps 1/2 thru NPS 24

ASME B16.11		(1996) Forged Fittings, Socket-Welding and Threaded

ASME B16.15	(1985; R 1994) Cast Bronze Threaded Fittings Classes 125 & 250

ASME B16.39 	(1986; R1994) Malleable Iron Threaded Pipe Unions Classes 150, 250, & 300

ASME B40.1		(1991) Gauges - Pressure Indicating Dial Type - Elastic Element

ASME BPV IX	(1998) Boiler & Pressure Vessel Code; Section IX, Welding & Brazing Qualifications

ASME PTC 19.3	(1974; R 1986) Instruments & Apparatus: Part 3 Temperature Measurement

ASME B16.34		(1997) Valves - Flanged, Threaded, and Welding End

ASME B31.3		(1999) Process Piping

ASME BPV VIII Div 1 (1998) Boiler and Pressure Vessel Code; Section VIII, Pressure Vessels Division 1 - Basic Coverage

ASME B31.1		(1998) Power Piping

ASME BPVC SEC IX  (1998) Boiler and Pressure Vessel Code; Section IX, Welding and Brazing Qualifications

ASME BPVC SEC VIII D1	(1998) Boiler and Pressure Vessel Code; Section VIII, Pressure Vessels Division 1 - Basic Coverage

ASME BPVC SEC	 (1998) Boiler and Pressure Vessel Codes

ASME BPVC IV	(1995; Addenda 1995 and 1996) Boiler and Pressure Vessel Code: Section IV Heating Boilers

ASME A112.14.1 	(1975; R 1998) Backwater Valves

ASME CSD-1 	            (2002) Control and Safety Devices for Automatically Fired Boilers

AMERICAN SOCIETY FOR TESTING AND MATERIALS (ASTM)

ASTM A 27/A 27M 	(1996) Steel Castings, Carbon, for General Application

ASTM A 167 	(1999) Stainless & Heat-Resisting Chromium-Nickel Steel Plate, Sheet, & Strip

ASTM A 182/A 182M (1998a) Forged or Rolled Alloy-Steel Pipe Flanges, Forged Fittings, and Valves and Parts for High-Temperature Service

ASTM A 193/A 193M 	(1999) Alloy-Steel and Stainless Steel Bolting Materials for High-Temperature Service

ASTM A 194/A 194M 	(1998b) Carbon and Alloy Steel Nuts for Bolts for High-Pressure and High-Temperature Service

ASTM A 216/A 216M 	(1998) Steel Castings, Carbon, Suitable for Fusion Welding, for High-Temperature Service

ASTM A 234/A 234M 	(1999) Piping Fittings of Wrought Carbon Steel and Alloy Steel for Moderate and High Temperature Service

ASTM A 269 	(1996) Seamless & Welded Austenitic Stainless Steel Tubing for General Service

ASTM A 312/A 312M	(1999) Seamless and Welded Austenitic Stainless Steel Pipes

ASTM A 403/A 403M	(1999) Wrought Austenitic Stainless Steel Piping Fittings

ASTM A 36/A 36M	(1997a) Carbon Structural Steel

ASTM A 48M		(1994) Gray Iron Castings (Metric)

ASTM A 53 	(1997) Pipe, Steel, Black & Hot-Dipped, Zinc-Coated, Welded & Seamless

ASTM A 123/A 123M 	(1997ael) Zinc (Hot-Dip Galvanized) Coatings on Iron & Steel Products

ASTM A 307 	(1997) Carbon Steel Bolts and Studs, 60 000 PSI Tensile Strength

ASTM A 366/A 366M 	(1996) Steel, Sheet, Carbon, Cold-Rolled, Commercial Quality

ASTM A 536 		(1984; R 1999el) Ductile Iron Castings

ASTM A 569/A 569M	(1997) Commercial Steel (CS) Sheet and Strip, Carbon (0.15 Maximum Percent), Hot-Rolled

ASTM A 653/A 653M	(1997) Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot-Dip Process

ASTM A 733 	(1993) Welded and Seamless Carbon Steel and Austenitic Stainless Steel Pipe Nipples

ASTM A 74 		(1998) Cast Iron Soil Pipe and Fittings

ASTM B 209M 	(1995) Aluminum and Aluminum-Alloy Sheet and Plate (Metric)

ASTM B 280 	(1997) Seamless Copper Tube for Air Conditioning & Refrigeration Field Service

ASTM B 117		(1997) Operating Salt Spray (Fog) Apparatus

ASTM B 32		(1996) Solder Metal

ASTM C 27		(1993) Fireclay and High-Alumina Refractory Brick

ASTM C 155		(1997) Standard Classification of Insulating Firebrick

ASTM C 195		(1995) Mineral Fiber Thermal Insulating Cement

ASTM C 196	(1993) Expanded or Exfoliated Vermiculate Thermal Insulating Cement

ASTM C 270		(1997a) Mortar for Unit Masonry

ASTM C 401	(1991; R 1995)) Alumina & Alumina-Silicate Castable Refractories

ASTM C 612		(1993) Mineral Fiber Block and Board Thermal Insulation

ASTM C 449/C 449M (1995) Mineral Fiber Hydraulic-Setting Thermal Insulating & Finishing Cement

ASTM C 534 	(1999) Preformed Flexible Elastomeric Cellular Thermal Insulation in Sheet & Tubular Form

ASTM C 547		(1995) Mineral Fiber Pipe Insulation

ASTM C 552		(1991) Cellular Glass Thermal Insulation

ASTM C 553 	(1992) Mineral Fiber Blanket Thermal Insulation for Commercial & Industrial Applications

ASTM C 564 		(1997) Rubber Gaskets for Cast Iron Soil Pipe and Fittings

ASTM C 592 	(1980) Mineral Fiber Blanket Insulation and Blanket-Type Pipe Insulation (Metal-Mesh Covered) (Industrial Type)

ASTM C 610 	(1995) Molded Expanded Perlite Block and Pipe thermal Insulation

ASTM C 647 	(1995) Properties & Tests of Mastics&Coating Finishes for Thermal Insulation

ASTM C 795 	(1998el) Thermal Insulation for Use in Contact With Austenitic Stainless Steel

ASTM C 916 		(1985; R 1996e1) Adhesives for Duct Thermal Insulation

ASTM C 920 		(1998) Elastomeric Joint Sealants

ASTM C 921 	(1989; R 1996) Determining the Properties of Jacketing Materials for Thermal Insulation

ASTM C 94		(1997) Ready-Mixed Concrete

ASTM C 1053 	(2000) Borosilicate Glass Pipe & Fittings for Drain, Waste, & Vent (DWV) Applications

ASTM C 1071 	(1991) Standard Specification for Thermal and Acoustical Insulation (Glass Fiber, Duct Lining Material)

ASTM C 1126	(1998) Faced or Unfaced Rigid Cellular Phenolic Thermal Insulation

ASTM C 1136	(1995) Flexible, Low Permeance Vapor Retarders for Thermal Insulation

ASTM C 1290	(1995) Flexible Fibrous Glass Blanket Insulation Used to Externally Insulate HVAC Ducts

ASTM D 975		(1998b) Diesel Fuel Oils

ASTM D 1384		(1996) Corrosion Test for Engine Coolants in Glass Ware

ASTM D 471		(1996) Rubber Property - Effect of Liquids

ASTM D 2240		(1997) Rubber Property - Durometer Hardness

ASTM D 2000		(1999) Rubber Products in Automotive Applications

ASTM D 3308		(1997) PTFE Resin Skived Tape

ASTM D 520		(2000) Zinc Dust Pigment

ASTM D 396		(1996) Fuel Oils

ASTM D 888		(1992; R 1996) Dissolved Oxygen in Water

ASTM D 2564 	(1996; Rev. A) Solvent Cements for Poly (Vinyl Chloride) (PVC) Plastic Piping Systems

ASTM D 257 	(1993) Standard Test Methods for D-C Resistance or Conductance of Insulating Materials

ASTM D 2665 	(1996) Poly(Vinyl Chloride) (PVC) Plastic Drain, Waste, & Vent Pipe & Fittings

ASTM D 635 	(1997) Rate of Burning and/or Extent and Time of Burning of Self-Supporting Plastics in a Horizontal Position

ASTM D 1693		(1997a) Environmental Stress-Cracking of Ethylene Plastics

ASTM E 1		(2001) ASTM Thermometers

ASTM E 84		(1999) Surface Burning Characteristics of Building Materials

ASTM E 96		(1995) Water Vapor Transmission of Materials

ASTM F 441/F 441M	(1999) Chlorinated Poly (Vinyl Chloride) (CPVC) Plastic Pipe, Schedules 40 and 80

ASTM F 493 	(1997) Solvent Cements for Chlorinated Poly(Vinyl Chloride) (CPVC) Plastic Pipe and Fittings

ASTM F 1097 	(1991; R 1996) Mortar, Refractory (High-Temperature, Air-Setting)

ASTM F 1199 	(1988; R 1998) Cast (All Temperature and Pressures) and Welded Pipe Line Strainers (150 psig and 150 degrees F Maximum)

ASTM F 1200 	(1988; R 1998) Fabricated (Welded) Pipe Line Strainers (Above 150 psig and 150 degrees F)

ASTM F 1007 	(1986; R 1996) Pipe-Line Expansion Joints of the Packed Slip Type for Marine Application

AMERICAN WELDING SOCIETY (AWS)

AWS A5.1		(1991) Carbon Steel Electrodes for Shielded Metal Arc Welding

AWS A5.28		(1996) Low Alloy Steel Filler Metals for Gas Shielded Arc Welding

AWS A5.4		(1992) Stainless Steel Electrodes for Shielded Metal Arc Welding

AWS A5.8		(1992) Filler Metals for Brazing and Braze Welding

AWS B2.1		(1984) Welding Procedure and Performance Qualification

AWS B2.2		(1991) Brazing Procedure and Performance Qualification

AWS D1.1		(1996) Structural Welding Code - Steel

AWS Z49.1		(1999) Safety in Welding and Cutting

AMERICAN WATER WORKS ASSOCIATION (AWWA)

AWWA EWW	(1999) Standard Methods for the Examination of Water & Wastewater

AWWA B300		(1999) Hypochlorites

AWWA B301		(1992; addenda B301a - 1999) Liquid Chlorine

AWWA C104	(1995) Cement-Mortar Lining for Ductile-Iron Pipe & Fittings for Water

AWWA C110 	(1998) Ductile-Iron and Gray-Iron Fittings, 3 In. Through 48 In. (75 mm through 1200 mm), for Water and Other Liquids

AWWA C111	(1995) Rubber-Gasket Joints for Ductile-Iron Pressure Pipe & Fittings

AWWA C151	(1996) Ductile-Iron Pipe, Centrifugally Cast, for Water or Other Liquids

AWWA C203 	(1997; addenda C203a - 1999) Coal-Tar Protective Coatings and Linings for Steel Water Pipelines - Enamel and Tape - Hot-Applied

AWWA C606		(1997) Grooved and Shouldered Joints

AWWA D100		(1996) Welded Steel Tanks for Water Storage

AWWA M20		(1973) Manual:  Water Chlorination Principles and Practices

### BRITISH STANDARDS INSTITUTION

BS 3505 		(1968; R 1982) Un-plasticized PVC pipe for cold-water services

BS 5169 		(1975) Fusion-welded steel receivers

BS 3790	(1981) Specification for endless wedge belt drives & endless V-belt drives

BS 143 /BS 1256 	(1968) Malleable cast iron & cast copper alloy screwed pipe fittings for steam, air, water, gas and oil

BS 1212 		(1970) Specifications for float operated valves (excluding floats)

BS 1247 		(1975) Manhole step irons

BS 1256 		(1968) See BS-143

BS 1387 	(1967) Steel tubes and tubulars suitable for screwing to BS 21 pipe threads

BS 159			(1957) Busbars and busbar connections

BS 162			(1961) Electric power switchgear and associated appaeatus

BS 21	(1973) Pipe threads for tubes & fittings where pressure-tight joints are made on threads

BS 2870 	(1980) Specification for rolled copper & copper alloys; sheet, strip & foil

BS 2871 		(1971, 1972) Copper and copper alloy, Tubes

BS 2989 	(1982) Specification for continuously hot-dip zinc coated & iron-zinc alloy coated steel: wide strip, sheet / plate and slit wide strip

BS 3402		(1969) Quality of vitreous china sanitary appliances

BS 3535	(1962) Safety isolating transformers for industrial & domestic purposes

BS 4504	(1969) Flanges & bolting for pipes, valves & fittings. Metric series

BS 4514	(1969) Unplasticized PVC soil & venting pipe, fittings & accessories

BS 4660		(1973) Unplasticized PVC underground drain pipe and fittings

BS 4752 	(1977) Specification for switchgear and control gear for voltages up to and including 1000-VAC and 1200-VDC

BS 4794	(1979) Specification for control switches (switching devices, including contactor relays, for control and auxiliary circuits, for voltages up to and including 1000-VAC and 1200-VDC)

BS 4941	(1977, 1979) Specification for motor starters for voltages up to & including 1000-VAC and 1200-VDC

BS 497	(1976) Specification for manhole covers, road gully grating & frames for drainage purposes

BS 5150	(1974) Cast iron wedge & double disk gate valves for general purposes

BS 5151		(1974) Cast iron gate (parallel slide) valves for general purposes

BS 5152	(1974) Cast iron globe & globe stop & check valves for general purposes

BS 5153		(1974) Cast iron check valves for general purposes

BS 5154	(1974) Copper alloy globe, glob stop & check, check, & gate valves

BS 5155	(1974) Cast iron & carbon steel butterfly valves for general purposes

BS 5158		Cast iron and carbon steel plug valves for general purposes

BS 5159		Cast iron and carbon steel ball valves for general purposes

BS 5160	(1977) Specification for flanged steel globe valves, globe stop valves, globe stop & check valves & lift type valves for general purposes

BS 5169		(1975) Fusion-welded steel air receivers

BS 5255		(1976) Plastic waste pipe and fittings

BS 5372	(1976) Specification for cable termination for electrical equipment

BS 5419	(1977) Specification for air-break switches, air-break disconnectors, air-break switch disconnectors & fuse combination units for voltages up to and including 1000-VAC and 1200-VDC

BS 5420	(1977) Specification for degree of protection of enclosures of switchgear & control gear for voltages up to & including 1000-VAC & 1200-VDC

BS 5424	(1977) Specification for control gear for voltages up to and including 1000-VAC and 1200-VDC

BS 5481	(1977) Specifications for unplasticized PVC pipe and fittings for gravity sewer

BS 5486	(1977) Specifications for factory-built assemblies of switchgear & control gear for voltages up to & including 1000-VAC & 1200-VDC

BS 5490	(1977) Specification for degree of protection provided by enclosures

BS 5500		(1982) Unfired fusion welded pressure vessels

BS 5572		(1978) Code of practice for sanitary pipework (formerly CP 304)

BS 5750		Refer to ISO9001:2000

BS 5955	(1980) Code of practice for plastic pipework (thermoplastics material)

BS 6283		Safety devices for use in hot water systems

BS 853	(1981) Specifications for calorifiers & storage vessels for central heating and hot water supply

BS CP 301		(1971) Code of practice for building drainage

CODE OF FEDERAL REGULATIONS (CFR)

47 CFR 15		Radio Frequency Devices

U.S. NATIONAL ARCHIVES AND RECORDS ADMINISTRATION (NARA)

29 CFR 1910		Occupational Safety and Health Standards

29 CFR 1910.104 	Oxygen

COPPER DEVELOPMENT ASSOCIATION (CDA)

CDA A4015		Copper Tube Handbook

COMPRESSED GAS ASSOCIATION (CGA)

CGA G-8.1		(1990) Nitrous Oxide Systems at Consumer Sites

CGA P-2.1	(1983) Medical-Surgical Vacuum Systems in Health Care Facilities

CGA V-1	(1994; Addenda 1996) Compressed Gas Cylinder Valve Outlet and Inlet Connections

CGA V-5	(1989) Diameter-Index Safety System (Non-Interchangeable Low Pressure Connections for Medical Gas Applications)

FACTORY MUTUAL ENGINEERING AND RESEARCH (FM)

FM P7825b		(1998) Approval Guide Electrical Equipment

FM P7825a		(1998) Approval Guide Fire Protection

U.S. GENERAL SERVICES ADMINISTRATION (GSA)

FS A-A-1689		(Rev. B) Tape, Pressure-Sensitive Adhesive, (Plastic Film)

FS A-A-50560		Pumps, Centrifugal, Water Circulating, Electric-Motor-Driven

FS A-A-50494		Exhaust Head, Steam

FS A-A-50544		Radiators, Heating, Steam and Hot Water, Cast Iron

FS WW-T-696		(Rev. E) Traps, Steam and Air

FS WW-S-2739		Strainers, Sediment:  Pipeline, Water, Air, Gas, Oil, or Steam

HYDRAULIC INSTITUTE (HI)

HI1.1-1.5		(1994) Standards for Centrifugal Pumps

### UNITED KINGDOM DEPARTMENT OF HEALTH, National Health Service

HTM 2022	(1997) Medical Gas pipeline systems, Health Technical Memorandum

HTM 2027	(1995) Hot & cold water supply, storage & mains services, Health Technical Memorandum

### INTERNATION CODE COUNCIL

ICC-Pluming Code	(1997) International pluming code

INSTITUTE OF ELECTRICAL AND ELECTRONICS ENGINEERS (IEEE)

IEEE C62.41		(1991; R 1995) Surge Voltages in Low-Voltage AC Power Circuits

ISA (ISA)

ISA MC96.1		(1982) Temperature Measurement Thermocouples

### INTERNATIONAL ORGANIZATION FOR STANDERIZATION

ISO 9001		(2000) Quality Assurance Management Systems

JORDANIAN NATIONAL CONSTRUCTION COUNCLE (JCC)

JCC-13		(1990) Jordanian Code for Thermal Insulation

JCC-15		(1990) Jordanian Code for Fire Protection in Buildings

JCC-137		(1980) Jordanian Standard Specifications

JCC-29		(1990) Jordanian Code for Central Heating

JCC-Mech. Services	(1985) Jordanian Code for Mechanical Services for Buildings

JCC-Drainage		(1988) Jordanian Code for Drainage of Buildings

JCC-Water Supply	(1988) Jordanian Code for Water Supply to Buildings

MIDWEST INSULATION CONTRACTORS ASSOCIATION (MICA)

MICA Insulation Stds	(1993) National Commercial & Industrial Insulation Standards

U.S. DEPARTMENT OF DEFENSE (DOD)

MIL-STD-282	(Basic, Notice 4) Filter Units, Protective Clothing, Gas-Mask Components and Related Products:  Performance-Test Methods

MIL-V-16733		(Rev. D) Valves, Pressure Regulating, Steam

MIL-V-18436		(Rev. F) Valves, Check:  Bronze, Cast-Iron, and Steel Body

MIL-V-18499		(Rev. E) Valves, Air Venting, Steam

MIL-V-18634		(Rev. B) Valves:  Safety, Relief, and Safety-Relief

MANUFACTURERS STANDARDIZATION SOCIETY OF THE VALVE AND FITTINGS INDUSTRY (MSS)

MSS SP-110	(1996) Ball Valves Threaded, Socket-Welding, Solder Joint, Grooved and Flared Ends

MSS SP-25	(1998) Standard Marking System for Valves, Fittings, Flanges & Unions

MSS SP-58	(1993) Pipe Hangers and Supports - Materials, Design and Manufacture

MSS SP-67		(1995) Butterfly Valves

MSS SP-69		(1996) Pipe Hangers and Supports - Selection and Application

MSS SP-70		(1998) Cast Iron Gate Valves, Flanged and Threaded Ends

MSS SP-71	(1997) Gray Iron Swing Check Valves, Flanges and Threaded Ends

MSS SP-72	(1999) Ball Valves with Flanged or Butt-Welding Ends for General Service

MSS SP-78		(1998) Cast Iron Plug Valves, Flanged and Threaded Ends

MSS SP-80		(1997) Bronze Gate, Globe, Angle and Check Valves

MSS SP-85	(1994) Cast Iron Globe & Angle Valves, Flanged and Threaded Ends

MSS SP-88		(1993) Diaphragm Type Valves

MSS SP-89	(1998) Pipe Hangers& Supports-Fabrication & Installation Practices

NATIONAL BOARD OF BOILER AND PRESSURE VESSEL INSPECTORS (NBBPVI)

NBBPVI NB-27		(1991) Boiler Blowoff System

NATIONAL ELECTRICAL MANUFACTURES ASSOCIATION (NEMA)

NEMA MG 1		(1993; Rev 1; Rev 2; Rev 3) Motors and Generators

NEMA 250	(1991) Enclosures for Electrical Equipment (1000 Volts Maximum)

NEMA ICS 1		(1993) Industrial Control and Systems

NEMA ICS 2	(1993) Industrial Control & Systems Controllers, Contactors& Over-load Relays, Rated Not More Than 2000 Volts AC or 750 Volts DC

NEMA ICS 6		(1993) Industrial Control and Systems Enclosures

NATIONAL FIRE PROTECTION ASSOCIATION (NFPA)

NFPA 13		(1999) Installation of Sprinkler Systems

NFPA 20	(1996; Errata Oct 1996; TIA 96-1) Installation of Centrifugal Fire Pumps

NFPA 30	(1996; Errata; TIA 96-2) Flammable and Combustible Liquids Code

NFPA 31		(1997; TIA 97-11) Installation of Oil Burning Equipment

NFPA 37	(1998) Installation & Use of Stationary Combustion Engines & Gas Turbines

NFPA 54		(1999) National Fuel Gas Code

NFPA 70		(1999) National Electrical Code

NFPA 54/ANSI Z223.1 	(1996; Errata) National Fuel Gas Code

NFPA 82	(1994) Incinerators, Waste & Linen Handling Systems & Equipment

NFPA 90A		(1999) Installation of Air Conditioning and Ventilating Systems

NFPA 91		(1995) Exhaust Systems for Air Conveying of Materials

NFPA 99		(1996) Health Care Facilities

NFPA 211	(1996; Errata 96-1) Chimneys, Fireplaces, Vents & Solid Fuel-Burning Appliances

NFPA 1963		(1998) Fire Hose Connections

PLASTIC PIPE AND FITTINGS ASSOCIATION (PPFA)

PPFA-01		(1998) Plastic Pipe in Fire Resistive Construction

SOCIETY OF AUTOMOTIVE ENGINEERS (SAE)

SAE AMS 2480E		(1992) Phosphate Treatment Paint Base

SAE J1508		(1997) Hose Clamp Specifications

SHEET METAL & AIR CONDITIONING CONTRACTORS' NATIONAL ASSOCIATION (SMACNA)

SMACNA Ind. Practice	(1975) Accepted Industry Practice for Industrial Duct Construction

SMACNA Arch. Manual 	(1993) Architectural Sheet Metal Manual

SMACNA DCS 		(1985) HVAC Duct Construction Standards - Metal and Flexible

SMACNA Seismic Mnl. 	(1991; Errata 1993) Seismic Restraint Manual Guidelines for  	Mechanical Systems

SMACNA Leakage Test Mnl (1985) HVAC Air Duct Leakage Test Manual

SMACNA RIDCS		(1980) Rectangular Industrial Duct Construction Standards

SMACNA RIDCSTD	(1977) Round Industrial Duct Construction Standards

SMACNA-06	(1995; 2nd Ed) HVAC Duct Construction Standards-Metal & Flexible

THE SOCIETY FOR PROTECTIVE COATINGS (SSPC)

SSPC Paint 21		(1991) White or Colored Silicone Alkyd Paint

SSPC Paint 25	(1991) Red Iron Oxide, Zinc Oxide, Raw Linseed Oil and Alkyd Primer (Without Lead and Chromate Pigments)

SSPC SP 5		(1994) White Metal Blast Cleaning

UNDERWRITERS LABORATORIES (UL)

UL 142	(1993; Rev Jul 1998) Steel Aboveground Tanks for Flammable and Combustible Liquids

UL 448		(1994; Rev thru May 1999) Pumps for Fire-Protection Service

UL 50			(1995; Rev Oct 1997) Enclosures for Electrical Equipment

UL 555		(1999; 6th Ed) UL Standard for Safety Fire Dampers

UL 567	(1996; Rev thru Oct 1997) Pipe Connectors for Petroleum Products & LP-Gas

UL 668	(1995; Rev thru Dec 1998) Hose Valves For Fire Protection Service

UL 94	(1996; Rev thru Jul 1998) Tests for Flammability of Plastic Materials for Parts in Devices and Appliances

UL Bld Mat Dir	(1999) Building Materials Directory

UL Fire Prot Dir	(1999) Fire Protection Equipment Directory

1.2   	ORDERING INFORMATION

The addresses of the organizations whose publications are referenced in other sections of these specifications are listed below, and if the source of the publications is different from the address of the sponsoring organization, that information is also provided.  Documents listed in the specifications with numbers which were not assigned by the sponsoring organization should be ordered from the source by title rather than by number.

AIR CONDITIONING AND REFRIGERATION INSTITUTE (ARI)

4301 North Fairfax Dr., Suite 425

ATTN:  Pubs Dept.

Arlington, VA  22203

Ph:  703-524-8800

Fax:  703-528-3816

E-mail:  ari@ari.org

Internet: www.ari.org

AIR MOVEMENT AND CONTROL ASSOCIATION (AMCA)

30 W. University Dr.

Arlington Heights, IL  60004-1893

Ph:  847-394-0150

Fax:  847-253-0088

Internet:  www.amca.org

AMERICAN ASSOCIATION OF STATE HIGHWAY AND TRANSPORTATION OFFICIALS (AASHTO)

444 N. Capital St., NW, Suite 249

Washington, DC  20001

Ph:  800-231-3475 202-624-5800

Fax:  800-525-5562 202-624-5806

Internet:  www.aashto.org

AMERICAN BOILER MANUFACTURERS ASSOCIATION (ABMA)

950 North Glebe Road, Suite 160

Arlington, Virginia 22203-1824

Ph:703-522-7350

Fax:  703-522-2665

Internet:  abma.com

AMERICAN INSTITUTE OF STEEL CONSTRUCTION (AISC)

One East Wacker Dr., Suite 3100

Chicago, IL  60601-2001

Ph:  312-670-2400

Publications: 800-644-2400

Fax:  312-670-5403

Internet:  www.aisc.org

AMERICAN NATIONAL STANDARDS INSTITUTE (ANSI)

11 West 42nd St

New York, NY  10036

Ph:  212-642-4900

Fax:  212-398-0023

Internet:  www.ansi.org/

Note:  Documents beginning with the letter "S" can be ordered from:

Acoustical Society of America

P. O. Box 1020

Sweickley, PA  15143-9998

Ph:  412-741-1979

Fax:  412-741-0609

Internet: asa.aip.org

AMERICAN PETROLEUM INSTITUTE (API)

1220 L St., NW

Washington, DC  20005-4070

Ph:  202-682-8000

Fax:  202-962-4776

Internet:  http://www.api.org

AMERICAN SOCIETY FOR TESTING AND MATERIALS (ASTM)

100 Barr Harbor Drive

West Conshohocken, PA  19428-2959

Ph: 610-832-9585

Fax:  610-832-9555

Internet:  www.astm.org

AMERICAN SOCIETY OF HEATING, REFRIGERATING AND AIR-CONDITIONING ENGINEERS (ASHRAE)

1791 Tullie Cir., NE

Atlanta, GA  30329

Ph:  800-527-4723 or 404-636-8400

Fax:  404-321-5478

Internet:  http://www.ashrae.org

AMERICAN WATER WORKS ASSOCIATION (AWWA)

6666 West Quincy

Denver, CO  80235

Ph:  800-926-7337 - 303-794-7711

Fax: 303-347-0804

Internet:  www.awwa.org

AMERICAN WELDING SOCIETY (AWS)

550 N.W. LeJeune Road

Miami, FL  33126

Ph:  800-443-9353 - 305-443-9353

Fax:  305-443-7559

Internet: http://www.amweld.org

ASME INTERNATIONAL (ASME)

Three Park Avenue

New York, NY 10016-5990

Ph:  212-591-7722

Fax:  212-591-7674

Internet:  www.asme.org

ASSOCIATION FOR THE ADVANCEMENT OF MEDICAL INSTRUMENTATION (AAMI)

1110 N. Globe Rd., Suite 220

Arlington, VA 22201-5762

Ph:  703-525-4890

Fax: 703-525-1424

Internet:  www.aami.org

BRITISH STANDARDS INSTITUTION (BSi)

2Park Street.

LONDON, W1A 2BS

Ph:  01-629 9000

Telex: 266933 BSILON G

Internet:  www.bsi.org

CODE OF FEDERAL REGULATIONS (CFR)

Order from:

Government Printing Office

Washington, DC  20402

Ph:  202-512-1800

Fax:  202-275-7703

Internet:  http://www.gpo.gov

COMPRESSED GAS ASSOCIATION (CGA)

1725 Jefferson Davis Highway, Suite 1004

Arlington, VA  22202-4102

Ph:  703-412-0900

Fax:  703-412-0128

Internet: www.cganet.com

e-mail:  Customer_Service@cganet.com

COPPER DEVELOPMENT ASSOCIATION (CDA)

260 Madison Ave.

New York, NY 10016

Ph:  212-251-7200

Fax:  212-251-7234

E-mail:  http://www.copper.org

INTERNATIONAL CODE COUNCIL (ICC)

5203 Leesburg Pike, Suite 708

Falls Church, VA  22041

Ph:   703-931-4533

Fax:  703-379-1546

Internet: www.intlcode.org

DEPARTMENT OF DEFENSE (DOD)

Order from:

National Technical Information Service

5285 Port Royal Road

Springfield, VA  22161

Ph:  703-605-6040

FAX: 703-487-4639

FACTORY MUTUAL ENGINEERING AND RESEARCH (FM)

500 River Ridge Drive

Norwood, MA  02062

Ph:  781-440-8000

Ph:  (Toll-Free):  877-364-6726

Fax:  718-440-8742

Internet:  www.fmglobal.com

FEDERAL SPECIFICATIONS (FS)

Order from:

General Services Administration

Federal Supply Service Bureau

470 L'Enfant Plaza, S.W.

Washington, DC  20407

Ph:  202-619-8925

Fax:  202-619-8978

Internet:  http://pub.fss.gsa.gov/

GERMANY INSTITUTE FOR STANDARDIZATION (DIN)

BURGGRAFENSTRAE 6

POSTFACH 11 07

10787 BERLIN

GERMANY

Internet: www.gsf.de

Ph: 49-30-2601-2260

Fax: 49-30-2601-1231

HYDRAULIC INSTITUTE (HI)

9 Sylvan Way, Suite 180

Parsippany, NJ  07054-3802

Ph:  888-786-7744 or 973-267-9700

Fax:  973-267-9055

Internet: www.pumps.org

INSTITUTE OF ELECTRICAL AND ELECTRONICS ENGINEERS (IEEE)

445 Hoes Ln, P. O. Box 1331

Piscataway, NJ  08855-1331

Ph:  732-981-0060 OR 800-701-4333

Fax:  732-981-9667

Internet:  www.ieee.org

E-mail: customer.service@ieee.org

INTERNATIONAL CONFERENCE OF BUILDING OFFICIALS (ICBO)

5360 Workman Mill Rd.

Whittier, CA  90601-2298

Ph:  800-284-4406

Ph:  310-699-0541

Fax:  310-692-3853

Internet:  icbo.org

INTERNATIONAL ORGANIZATION FOR STANDARDIZATION (ISO)

1, rue de Varembe'

Case Postale 56

CH-1211 Geneve 20

Switzerland

Ph:  41-22-749-0111

Fax:  41-22-733-3430

Internet:  www.iso.ch

e-mail:  central@iso.ch

IRON & STEEL SOCIETY (ISS)

186 Thornhill Rd

Warrendale, PA  15086-7528

Ph:  724-776-1353 Ext 1

Fax: 724-776-0430

E-Mail:  custserv@issource.org

Internet:  www.issource.org

ISA (ISA)

67 Alexander Drive

P.O. Box 12277

Research Triangle Park, NC  27709

Ph:  919-549-8411

Fax:  919-549-8288

e-mail:  ISA@isa.org

Internet:  http://www.isa.org

JORDANIAN NATIONAL CONSTRUCTION COUNCLE (JCC)

Order from:

Union of Jordanian Engineers

Amman, Shmaisani

Jordan

MANUFACTURERS STANDARDIZATION SOCIETY OF THE VALVE AND FITTINGS INDUSTRY (MSS)

127 Park St., NE

Vienna, VA  22180-4602

Ph:  703-281-6613

Fax:  703-281-6671

Internet:  www.mss-hq.com

e-mail:  info@mss-hq.com

MIDWEST INSULATION CONTRACTORS ASSOCIATION (MICA)

2017 So. 139th Cir.

Omaha, NE  68144

Ph:  402-342-3463

Fax:  402-330-9702

Internet:  www.micainsulation.org

e-mail:  info@micainsulation.org

MILITARY STANDARDS (MIL-STD)

Order from:

Standardization Documents Order Desk

Building 4, Section D

700 Robbins Ave.

Philadelphia, PA 19111-5094

Ph:  215-697-2179

Fax:  215-697-2978

Internet:  www.dodssp.daps.mil

NATIONAL BOARD OF BOILER AND PRESSURE VESSEL INSPECTORS (NBBPVI)

1055 Crupper Ave.

Columbus, OH  43229-1183

Ph:  614-888-2463

Fax:  614-847-1147

Internet:  www.nationalboard.org

e-mail: orders@nationalboard.org

NATIONAL ELECTRICAL MANUFACTURERS ASSOCIATION (NEMA)

1300 N. 17th St., Suite 1847

Rosslyn, VA  22209

Ph: 703-841-3200

Fax:  703-841-3300

Internet:  http//www.nema.org/

NATIONAL ENVIRONMENTAL BALANCING BUREAU (NEBB)

8575 Grovemont Circle

Gaithersburg, MD  20877-4121

Ph:  301-977-3698

Fax:  301-977-9589

Internet:  www.nebb.org

NATIONAL FIRE PROTECTION ASSOCIATION (NFPA)

1 Batterymarch Park

P.O. Box 9101

Quincy, MA  02269-9101

Ph: 617-770-3000

Fax:  617-770-0700

Internet:  www.nfpa.org

NATIONAL INSTITUTE FOR OCCUPATIONAL SAFETY AND HEALTH (NIOSH)

Mail Stop C-13

4676 Columbia Parkway

Cincinnati, OH  45226-1998

Ph:  800-356-4676

Internet:  http://www.cdc.gov/niosh/homepage.html

SHEET METAL & AIR CONDITIONING CONTRACTORS' NATIONAL ASSOCIATION (SMACNA)

4201 Lafayette Center Dr.,

Chantilly, VA  20151-1209

Ph:  703-803-2980

Fax:  703-803-3732

Internet:  http://www.smacna.org

e-mail: info@smacna.org

SOCIETY OF AUTOMOTIVE ENGINEERS (SAE)

400 Commonwealth Dr.

Warrendale, PA  15096-0001

Ph:  724-776-4841

Fax:  724-776-5760

Internet:  http://www.sae.org

e-mail:  publications@sae.org

UNDERWRITERS LABORATORIES (UL)

333 Pfingsten Rd.

Northbrook,  IL  60062-2096

Ph:  847-272-8800

Fax: 847-272-8129

Internet:  http://www.ul.com/

e-mail:  northbrook@us.ul.com

End Of Section

SECTION: 1

##### GENERAL CONDITIONS AND REQUIREMENTS

##### FOR MECHANICAL WORKS

# PART 1   GENERAL

## 1.1   Scope

The following General Conditions and Requirement particularly relate to the Mechanical Engineering aspects of the Contract. They shall be read and interpreted in conjunction with all other Sections of the Specification, the Drawings, the Schedules and all other documents forming part of the Tender Documents.

This section applies to all sections of Mechanical Specifications of this project, except where modified therein.

## 1.2   	Modification of References

In each of the publications referred to in mechanical specifications, consider the advisory provisions to be mandatory, as though the word, "shall" had been substituted for "should" wherever it appears.  Interpret references in these publications to the "authority having jurisdiction", or words of similar meaning, to mean the Engineer.

The publications listed in all Mechanical sections form a part of Mechanical Specifications to the extent referenced.  The publications are referred to in the text by basic designation only.  Due to the nature of the local market, and where alternative brands are of equivalent quality and meet internationally recognized standards or codes of practice, the Contractor shall be permitted to submit such brands subject to the approval of the Engineer. At the discretion of the Engineer, the Contractor will be required to furnish test reports pertaining to any of the tests necessary to assure compliance with the standard or standards referenced in this specification.

## 1.3   	EXTERNAL DESIGN CONDITIONS

The design environmental conditions for Gasa are as follows:

Summer Design Temperature		: 35 C dry bulb, 31.0 C wet bulb

Absolute Maximum Temperature		: 38 C dry bulb

Winter Design Temperature      		:   5.0 C  dry bulb

## 1.4   	EQUIPMENT

### 1.4.1   EQUIPMENT RATINGS

All equipment selected for use on this Contract shall be suitable for continuous and reliable operation under the external design conditions stated. In addition, items of equipment installed in enclosed spaces may be subject to temperatures in excess of those prevailing externally and this shall be taken into account. Where ratings are given in this Specification and/or shown on the Drawings, they are the actual ratings to be achieved after the application of all de-rating factors.

All equipment and enclosures that may be subject to internal condensation shall be fitted with suitably rated electrically operated thermostatically controlled anti-condensation heaters.

### 1.4.2   	Material and Equipment Qualifications

Provide materials and equipment that are standard products of manufacturers regularly engaged in the manufacture of such products, which are of a similar material, design and workmanship. Standard products shall have been in satisfactory commercial or industrial use for minimum 5 years prior to bid opening.  The 5-year use shall include applications of equipment and materials under similar circumstances and of similar size.  The product shall have been for sale on the commercial market through advertisements, manufacturers' catalogs, or brochures during the 5 year period

### 1.4.3   	Alternative Qualifications:

Products having less than a five-year field service record will be acceptable if a certified record of satisfactory field operation for not less than 6000 hours, exclusive of the manufacturer's factory or laboratory tests, can be shown.

### 1.4.4   	Service Support

The equipment items shall be supported by service organizations.  Submit a certified list of qualified permanent service organizations for support of the equipment, which includes their addresses and qualifications.  These service organizations shall be reasonably convenient to the equipment installation and able to render satisfactory service to the equipment on a regular and emergency basis during the warranty period of the contract

### 1.4.5   	Manufacturer's Nameplate

Each item of equipment shall have a nameplate bearing the manufacturer's name, address, model number, and serial number securely affixed in a conspicuous place; the nameplate of the distributing agent will not be acceptable

## 1.5   	COORDINATION

The Contractor shall be responsible for all aspects of coordination necessary to ensure that the works are properly installed in accordance with the Contract Drawings and Specification. This shall include the inter relationship between Mechanical and Electrical Services, the Building Foundations, Fabrics and Finishes, and all Specialist Equipment contained therein, whether supplied under this Contract or not.

Coordination shall cover the programming and physical requirements of all works.  Particular care must be taken in the setting out of works in common ducts, tunnel, and false ceiling or similar areas accommodating several services. The disposition of services shall be such that necessary segregation is maintained and that the completed installation affords ready access at a later date for the replacement, maintenance and extension thereof.

## 1.6   	SUBMITTAL PROCEDURES

For all material, equipment and systems specified under Mechanical works, submittals shall be in accordance with this specifications, except where modified therein.

### 1.6.1   Verification of Dimensions

A letter, at least 2 weeks prior to beginning construction, including the date the site was visited, conformation of existing conditions, and any discrepancies found

### 1.6.2   Shop Drawings

At least 5 weeks prior to beginning construction, provided in adequate detail to demonstrate compliance with contract requirements.  Drawings shall consist of:

- Equipment layouts which identify assembly and installation details,

- Plans and elevations which identify clearances required for maintenance and operation

- Wiring diagrams which identify each component individually and all interconnected or interlocked relationships between components

- Foundation drawings, bolt-setting information, and foundation bolts prior to concrete foundation construction for all equipment indicated or required to have concrete foundations.

- Details, if piping and equipment are to be supported other than as indicated, which include loadings and type of frames, brackets, stanchions, or other supports

Each drawing shall have a blank area of 18 cm. x 12 cm. located adjacent to the title black and reserved for the comments of the Engineer. The title block shall display the following: -

Number and title of drawing (s),

Date of drawing or revision, Name of project and employer

Name of consultant,

Name of contractor and sub-contractor submitting the drawing(s)

Clear identification of contents and location of work

Specification title and number

Scale of drawings

The scale drawings shall be to a minimum scale of 1:50 and in complex areas, such as plant room and service ducts, scales of 1:20 and 1:10 shall be applied.

### 1.6.3   Product Data

#### 1.6.3.1   Manufacturer's standard catalog data

At least 5 weeks prior to the purchase or installation of a particular component, highlighted to show material, size, options, performance charts and curves, etc. in adequate detail to demonstrate compliance with contract requirements. Data shall include manufacturer's recommended installation instructions and procedures. If vibration isolation is specified for a unit, vibration isolator literature shall be included containing catalog cuts and certification that the isolation characteristics of the isolators provided meet the manufacturer's recommendations

#### 1.6.3.2 Spare Parts Spare parts data for each different item of equipment specified, after approval of detail drawings and not later than 3 months prior to the date of beneficial occupancy. The data shall include a complete list of parts and supplies, with current unit prices and source of supply, a recommended spare parts list for 1 year of operation, and a list of the parts recommended by the manufacturer to be replaced on a routine basis

#### 1.6.3.3   Posted Instructions

Posted instructions, at least 2 weeks prior to construction completion, including equipment layout, wiring and control diagrams, piping, valves and control sequences, and typed condensed operation instructions.  The condensed operation instructions shall include preventative maintenance procedures, methods of checking the system for normal and safe operation, and procedures for safely starting and stopping the mechanical systems. The posted instructions shall be framed under glass or laminated plastic and be posted where indicated by the Engineer.

#### 1.6.3.4 Manufacturer’s Warranty

Manufacturer's multi-year warranty for the following components shall be submitted 1-week prior to delivery of such equipments to site.

#### 1.6.3.5 Factory Tests

Schedules, at least 2 weeks prior to the factory test, which identify the date, time, and location for each test.  Schedules shall be submitted for both the Performance Test and the Sound Test of Chillers, Boilers, Medical Air Compressors, Vacuum Pumps and any other equipments as required by the Engineer.

### 1.6.4   Demonstrations A schedule, at least 2 weeks prior to the date of the proposed training course, which identifies the date, time, and location for the training

### 1.6.5   Test Reports

#### 1.6.5.1 Factory Tests Six copies of the report shall be provided in bound A4 booklets. Reports shall certify the compliance with performance requirements and follow the format of the required testing standard for both the Performance Tests and the Sound Tests. Test report shall include certified calibration report of all test instrumentation. Calibration report shall include certification that all test instrumentation has been calibrated within 6 months prior to the test date, identification of all instrumentation, and certification that all instrumentation complies with requirements of the test standard. Test report shall be submitted 1 week after completion of the factory test

#### 1.6.5.2 System Performance Tests

Six copies of the report shall be provided in bound A4 booklets. The report shall document compliance with the specified performance criteria upon completion and testing of the system. The report shall indicate the number of days covered by the tests and any conclusions as to the adequacy of the system. The report for HVAC system shall also include the following information and shall be taken at least three different times at outside dry-bulb temperatures that are at least 3 degrees C (5 degrees F) apart:

Date and outside weather conditions the load on the system based on the following: The refrigerant used in the system. Condensing temperature and pressure. Suction temperature and pressure. Running current, voltage and proper phase sequence for each phase of all motors the actual on-site setting of all operating and safety controls.

### 1.6.6   Certificates

Where the system, components, or equipment are specified to comply with requirements of a product certification scheme (such as UL, ASME, CE, FM .etc) 1 copy of proof of such compliance shall be provided.  The label or listing of the specified agency shall be acceptable evidence. In lieu of the label or listing, a written certificate from an approved, nationally recognized testing organization equipped to perform such services, stating that the items have been tested and conform to the requirements and testing methods of the specified agency may be submitted. For ARI rating, when performance requirements of this project's drawings and specifications vary from standard ARI rating conditions, computer printouts, catalog, or other application data certified by ARI or a nationally recognized laboratory as described above shall be included. If ARI does not have a current certification program that encompasses such application data, the manufacturer may self certify that his application data complies with project performance requirements in accordance with the specified test standards

#### 1.6.6.1   Service Organizations

A certified list of qualified permanent service organizations for support of the equipment, which includes their addresses and qualifications. The service organizations shall be reasonably convenient to the equipment installation & be able to render satisfactory service to the equipment on a regular & emergency basis during the warranty period of the contract

### 1.6.7   Operation and Maintenance Data

#### 1.6.7.1   Operation Manuals

Six complete copies of an operation manual in bound A4 booklets listing step-by-step procedures required for system startup, operation, abnormal shutdown, emergency shutdown, and normal shutdown at least 4 weeks prior to the first training course. The booklets shall include the manufacturer's name, model number, and parts list. The manuals shall include the manufacturer's name, model number, service manual, & a brief description of all equipment and their basic operating features

#### 1.6.7.2   Maintenance Manuals

Six complete copies of maintenance manual in bound A4 booklets listing routine maintenance procedures, possible breakdowns and repairs, and a trouble shooting guide. The manuals shall include piping and equipment layouts and simplified wiring and control diagrams of the system as installed

## 1.7   	ACCESSIBILITY

Install all work so that parts requiring periodic inspection, operation, maintenance, and repair are readily accessible. Install concealed valves, expansion joints, controls, dampers, and equipment requiring access, in locations freely accessible through access doors.

## 1.8   	SAFETY REQUIREMENTS

Exposed moving parts, parts that produce high operating temperature, parts which may be electrically energized, and parts that may be a hazard to operating personnel shall be insulated, fully enclosed, guarded, or fitted with other types of safety devices.  Safety devices shall be installed so that proper operation of equipment is not impaired.  Welding and cutting safety requirements shall be in accordance with AWS Z49.1

## 1.9   	DELIVERY, STORAGE, AND HANDLING

Stored items shall be protected from the weather, humidity and temperature variations, dirt and dust, or other contaminants. Proper protection and care of all material both before and during installation shall be the Contractor's responsibility. Any materials found to be damaged shall be replaced at the Contractor's expense. During installation, piping and similar openings shall be capped to keep out dirt and other foreign matter

## 1.10   	PROJECT/SITE CONDITIONS

### 1.10.1   Verification of Site Conditions

The Contractor shall become familiar with all details of the work, verify all dimensions in the field, and advise the Engineer of any discrepancy before performing any work

### 1.10.2   Design Drawings Review

Because of the small scale of the drawings, it is not possible to indicate all offsets, fittings, and accessories that may be required. The Contractor shall carefully investigate the plumbing, fire protection, electrical, structural and finish conditions that would affect the work to be performed and shall arrange such work accordingly, furnishing required offsets, fittings, and accessories to meet such conditions.

## 1.11   	SPARE PARTS AND TOOLS

A complete set of spare parts and their required tools shall be provided by the contractor to be used for any possible breakdown or where recommended by the manufacturer to be replaced on a routine basis of a 1-year operation.

## 1.12   	MANUFACTURER'S MULTI-YEAR WARRANTY

The warranties shall be directly from the manufacturer to the Owner and shall be in addition to the standard one-year warranty of construction. The manufacturer's warranty shall provide for the repair or replacement of the equipment/components that become inoperative as a result of defects in material or workmanship within the specified years after the date of final acceptance. When the manufacturer determines that a component requires replacement, the manufacturer shall furnish new components at no additional cost to the Owner.  Upon notification that a component/equipment has failed under the terms of the warranty, the manufacturer shall respond in no more than 24 hours.  Response shall mean having a manufacturer-qualified technician on site to evaluate the extent of the needed repairs. The warranty period shall begin on the same date as final acceptance and shall continue for the full product warranty period.

### 1.12.1   Scope

In addition to the warranties required in relevant sections, the following equipment shall be covered as minimum:

5-Years Warranty for Compressor(s) in Package units

5-Years Warranty for Medical Air Compressors

5-Years Warranty for Medical Vacuum Pumps

2-Years Warranty for Oil Fired Burners in Boilers 2-Years Warranty for Split AC Units

2-Years Warranty for Fans

2-Years Warranty for Calorifiers

2-years Warranty for Purified water tank

2-Years Warranty for Softeners

2-Years Warranty for Beg Filters

### 1.12.2 Indexed Notebook the Contractor shall furnish to the Engineer a bound and indexed notebook containing a complete listing of all similar equipments covered by a manufacturer's multi-year warranty. The equipment list shall state the duration of the warranty thereof, start date of the warranty, ending date of the warranty, location of the warranted equipment, and the point of contact for fulfillment of the warranty. Point of contact shall include the name of the service representative along with the day, night, weekend, and holiday phone numbers for a service call. The completed bound and indexed notebook shall be delivered to the Engineer prior to final acceptance of the facility.

### 1.12.3 	Local Service Representative: The Contractor shall furnish with each manufacturer's multi-year warranty the name, address, and telephone number (day, night, weekend, and holiday) of the service representative nearest to the location where the equipment is installed.  Upon a request for service under the multi-year warranty, the service representative shall honor the warranty during the warranty period, and shall provide the services prescribed by the terms of the warranty

### 1.12.4 	Equipment Warranty Tags at the time of installation, each item of manufacturer's multi-year warranted equipment shall be tagged with a durable, oil- and water-resistant tag, suitable for interior and exterior locations, resistant to solvents, abrasion, and fading due to sunlight. The tag shall be attached with copper wire or a permanent, pressure-sensitive, adhesive backing. The tag shall be installed in an easily noticed location attached to the warranted equipment.  The tag for this equipment shall be similar to the following in format, and shall contain all of the listed information:

MANUFACTURER'S MULTI-YEAR WARRANTY EQUIPMENT TAG

Equipment/Product Covered	:  	_____________________________

Manufacturer			:	_____________________________

Model No.			: 	______________

Serial No.			: 	_______________

Warranty Period		: 	From_____________ To: _________

Contract No.			:	_____ Warranty Contact: __________

Name				: ___________________________________ 	Address			:  ____________________________________ 	Telephone			:  ________________Fax:________________

STATION PERSONNEL SHALL PERFORM PREVENTIVE MAINTENANCE AND OPERATIONAL MAINTENANCE

## 1.13   	ELECTRICAL REQUIREMENTS

Furnish motors, controllers, disconnects and contactors with their respective pieces of equipment. Motors, controllers, disconnects and contactors shall conform to and have electrical connections provided under Electrical Specifications for this contract. Furnish internal wiring for components of packaged equipment as an integral part of the equipment. Extended voltage range motors will not be permitted. Controllers and contactors shall have a maximum of 220volt control circuits, and shall have auxiliary contacts for use with the controls furnished.  When motors and equipment furnished are larger than sizes indicated, the cost of additional electrical service and related work shall be included under the section that specified that motor or equipment.  Power wiring and conduit for field installed equipment shall be provided under and conform to the requirements of Electrical Specifications.

### 1.13.1   ELECTRICAL INSTALLATION REQUIREMENTS

All Electrical installations shall conform Electrical Specifications except where modified herein.

Provide electrical components of mechanical equipment, such as motors, motor starters, control or push-button stations, float or pressure switches, solenoid valves, integral disconnects, and other devices functioning to control mechanical equipment, as well as control wiring and conduit for circuits rated 220 volts or less, to conform with the requirements of the section covering the mechanical equipment. Extended voltage range motors shall not be permitted. The interconnecting power wiring and conduit, control wiring rated 220 volts (nominal) and conduit and the electrical power circuits shall be provided under Electrical Specifications, except internal wiring for components of package equipment shall be provided as an integral part of the equipment.  When motors and equipment furnished are larger than sizes indicated, provide any required changes to the electrical service as may be necessary and related work as a part of the work for the section specifying that motor or equipment.

#### 1.13.1.1 High Efficiency Single-Phase Motors

Unless otherwise specified, single-phase fractional-horsepower alternating-current motors shall be high efficiency types corresponding to the applications listed in NEMA MG 11.

#### 1.13.1.2   High Efficiency Poly phase Motors

Unless otherwise specified, poly phase motors shall be selected based on high efficiency characteristics relative to the applications as listed in NEMA MG 10. Additionally, poly phase squirrel-cage medium induction motors with continuous ratings shall meet or exceed energy efficient ratings in accordance with Table 12-6C of NEMA MG 1.

#### 1.13.1.3   Three-Phase Motor Protection

Provide controllers for motors rated one horsepower and larger with electronic phase-voltage monitors designed to protect motors from phase-loss, under voltage, and over voltage. Provide protection for motors from immediate restart by a time adjustable restart relay.

## 1.14   	TRAINING OF ENGINEERING STAFF

The Contractor shall provide training for the employees of the employer. Such training shall cover all aspects of using, running, commissioning and maintaining of all Engineering services.

# PART 2   PRODUCTS (Not used)

# PART 3   EXECUTION (Not used)

# End Of Section

SECTION: 2

###### THERMAL INSULATION FOR MECHANICAL SYSTEMS

# PART 1   GENERAL

This section applies to all Mechanical Specification Sections, whether referred to, or nor.

## 1.1   	SYSTEM DESCRIPTION

Field-applied insulation & accessories on mechanical systems shall be as specified herein; factory-applied insulation is specified under the piping, duct or equipment to be insulated.

## 1.2   	GENERAL QUALITY CONTROL

### 1.2.1   	Standard Products

Materials shall be the standard products of manufacturers regularly engaged in the manufacture of such products and shall essentially duplicate items that have been in satisfactory use for at least 2 years prior to bid opening.

### 1.2.2   	Installer's Qualifications

Qualified installers shall have successfully completed three or more similar type jobs within the last 5 years.

### 1.2.3   	Surface Burning Characteristics

Unless otherwise specified, insulation not covered with a jacket shall have a flame spread index no higher than 75 and a smoke developed index no higher than 150. Insulation systems which are located in air plenums, in ceiling spaces, and in attic spaces shall have a flame spread index no higher than 25 and a smoke developed index no higher than 50. Insulation materials located exterior to the building perimeter are not required to be fire-rated. Flame spread and smoke developed indexes shall be determined by ASTM E 84. Insulation shall be tested in the same density and installed thickness as the material to be used in the actual construction. Material supplied by a manufacturer with a jacket shall be tested as a composite material. Jackets, facings, and adhesives shall have a flame spread index no higher than 25 and a smoke developed index no higher than 50 when tested in accordance with ASTM E 84.

### 1.2.4   	Identification of Materials

Packages or standard containers of insulation, jacket material, cements, adhesives, and coatings delivered for use, and samples required for approval shall have manufacturer's stamp or label attached giving the name of the manufacturer and brand, and a description of the material.

1.3   	SUBMITTALS

Samples

Thermal Insulation Materials;

A complete list of materials, including manufacturer's descriptive technical literature, performance data, catalog cuts, & installation instructions. The product number, k-value, thickness & furnished accessories for each mechanical system requiring insulation shall be included. Materials furnished under this section of the specification shall be submitted at one time.

After approval of materials & prior to applying insulation a booklet shall be prepared & submitted for approval. The booklet shall contain marked-up MICA Insulation Stds plates (or detail drawings showing the insulation material & insulating system) for each pipe, duct, or piece of equipment required to be insulated per this specification. The MICA plates shall be marked up showing the materials to be installed in accordance with the requirements of this specification for the specific insulation application. The Contractor shall submit all MICA Plates required to show the entire insulating system, including Plates required to show insulation penetrations, vessel bottom & top heads, legs, & skirt insulation as applicable. If the Contractor elects to submit detailed drawings instead of marked-up MICA Plates, the detail drawings shall show cut-away, section views, & details indicating each component of the insulation system & showing provisions for insulating jacketing, & sealing portions of the equipment. For each type of insulation installation on the drawings, provide a label, which identifies each component in the installation (i.e., the duct, insulation, adhesive, vapor retarder, jacketing, tape, mechanical fasteners, etc.) Indicate insulation by type & manufacturer. Three copies of the booklet shall be submitted at the jobsite to the Engineer. One copy of the approved booklet shall remain with the insulation Contractor's display sample & two copies shall be provided for Owner use.

After approval of materials actual sections of installed systems properly insulated in accordance with the specification requirements shall be displayed.  Such actual sections must remain accessible to inspection throughout the job and will be reviewed from time to time for controlling the quality of the work throughout the construction site. Each material used shall be identified, by indicating on an attached sheet the specification requirement for the material and the material by each manufacturer intended to meet the requirement. Display sample sections will be inspected at the jobsite by the Engineer.  Approved display sample sections shall remain on display at the jobsite during the construction period. Upon completion of construction, the display sample sections will be closed and sealed.

Pipe Insulation Display Sections: Display sample sections shall include as a minimum an elbow or tee, a valve, dielectric unions and flanges, a hanger with protection shield and insulation insert, or dowel as required, at support point, method of fastening and sealing insulation at longitudinal lap, circumferential lap, butt joints at fittings and on pipe runs, and terminating points for each type of pipe insulation used on the job, and for hot pipelines and cold pipelines, both interior and exterior, even when the same type of insulation is used for these services.

Duct Insulation Display Sections: Display sample sections for rigid and flexible duct insulation used on the job. A display section for duct insulation exposed to weather shall be protected by enclosing with a temporary covering.

1.4   	STORAGE

Materials shall be delivered in the manufacturer's unopened containers. Materials delivered and placed in storage shall be provided with protection from weather, humidity, dirt, dust and other contaminants. Insulation material and supplies that become dirty, dusty, wet, or otherwise contaminated may be rejected by the Engineer.

# PART 2   PRODUCTS

## 2.1   	GENERAL MATERIALS

Materials shall be compatible and shall not contribute to corrosion, soften, or otherwise attack surfaces to which applied in either the wet or dry state. Materials to be used on stainless steel surfaces shall meet ASTM C 795 requirements.  Materials shall be asbestos free and conform to the following:

### 2.1.1   	Adhesives

#### 2.1.1.1   Acoustical Lining Insulation Adhesive

Adhesive shall be a nonflammable, fire-resistant adhesive conforming to ASTM C 916, Type I.

#### 2.1.1.2 Mineral Fiber Insulation Cement: Cement shall be in accordance with ASTM C 195.

#### 2.1.1.3   Lagging Adhesive

Lagging is the material used for thermal insulation, especially around a cylindrical object. This may include the insulation as well as the cloth/ material covering the insulation. Lagging adhesives shall be non flammable and fire-resistant and shall have a flame spread rating no higher than 25 and a smoke developed rating no higher than 50 when tested in accordance with ASTM E 84. Adhesive shall be pigmented white and be suitable for bonding fibrous glass cloth to faced and unfaced fibrous glass insulation board; for bonding cotton brattice cloth to faced and unfaced fibrous glass insulation board; for sealing edges of and bounding fibrous glass tape to joints of fibrous glass board; for bonding lagging cloth to thermal insulation; or for attaching fibrous glass insulation to metal surfaces.  Lagging adhesives shall be applied in strict accordance with the manufacturer's recommendations.

### 2.1.2   	Contact Adhesive

Adhesive may be dispersed in a non-halogenated organic solvent or, dispersed in a nonflammable organic solvent, which shall not have a fire point below 94 degrees C. The adhesive shall not adversely affect, initially or in service, the insulation to which it is applied, nor shall it cause any corrosive effect on metal to which it is applied. Any solvent dispersing medium or volatile component of the adhesive shall have no objectionable odor and shall not contain any benzene or carbon tetrachloride. The dried adhesive shall not emit nauseous, irritating, or toxic volatile matters or aerosols when the adhesive is heated to any temperature up to 100 degrees C. The adhesive shall be nonflammable and fire resistant.

### 2.1.3 Caulking: ASTM C 920, Type S, Grade NS, Class 25, Use A.

### 2.1.4   	Corner Angles

Nominal 0.4060mm (0.016 inch) aluminum 25x25mm with factory applied kraft backing.  Aluminum shall be ASTM B 209M, Alloy 3003, 3105, or 5005.

### 2.1.5   	Finishing Cement

Mineral fiber hydraulic-setting thermal insulating cement ASTM C 449/C 449M.  All cements that may come in contact with Austenitic stainless steel must include testing per ASTM C 795.

### 2.1.6   	Fibrous Glass Cloth and Glass Tape

Fibrous glass cloth and glass tape shall have flame spread and smoke developed ratings of no greater than 25/50 when measured in accordance with ASTM E 84.  Tape shall be 100mm wide rolls.

### 2.1.7   	Staples

Outward clinching type monel. Monel is a nickel rich alloy, which has high strength, high ductility, and excellent resistance to corrosion.

### 2.1.8   	Jackets

ASTM C921, Type I, maximum moisture vapor transmission 0.02 perms, (measured before factory application or installation), minimum puncture resistance 50 Beach units on all surfaces except concealed ductwork, where a minimum puncture resistance of 25 Beach units is acceptable. Minimum tensile strength, 6.1 N/mm (35 pounds/inch) width. ASTM C921, Type II, minimum puncture resistance 25 Beach units, tensile strength minimum 3.5 N/mm width.  Jackets used on insulation exposed in finished areas shall have white finish suitable for painting without sizing. Based on the application, insulation materials which require factory applied jackets are mineral fiber, cellular glass, & phenolic foam. All non-metallic jackets shall have a max. flame spread index of 25& a max. smoke developed index of 50 when tested in accordance with ASTM E 84.

#### 2.1.8.1   White Vapor Retarder All Service Jacket (ASJ)

For use on hot/cold pipes, ducts, or equipment vapor retarder jackets used on insulation exposed in finished areas shall have white finish suitable for painting without sizing.

#### 2.1.8.2   Aluminum Jackets

Aluminum jackets shall be corrugated, embossed or smooth sheet, 0.4060mm nominal thickness; ASTM B 209M, Temper H14, Temper H16, Alloy 3003, 5005, or 3105 with factory applied moisture retarder.  Corrugated aluminum jacket shall not be used outdoors. Aluminum jacket securing bands shall be Type 304 stainless steel, 0.3960mm thick, 12.7mm wide for pipe under 300mm diameter and 19.1mm (3/4 inch) wide for pipe over 300mm and larger diameter. Aluminum jacket circumferential seam bands shall be 50.8x0.4060mm aluminum matching jacket material. Bands for insulation below ground shall be 19.1x0.5080 mm thick stainless steel, or fiberglass reinforced tape. The jacket may, at the option of the Contractor, be provided with a factory fabricated Pittsburg or "Z" type longitudinal joint.  When the "Z" joint is used, the bands at the circumferential joints shall be designed by the manufacturer to seal the joints and hold the jacket in place.

### 2.1.9   Vapor Retarder Coating

The vapor retarder coating shall be fire and water resistant and appropriately selected for either outdoor or indoor service. Color shall be white. The water vapor permeance of the compound shall be determined according to procedure B of ASTM E 96 utilizing apparatus described in ASTM E 96. The coating shall be a nonflammable, fire resistant type. All other application and service properties shall be in accordance with ASTM C 647.

#### 2.1.9.1   Vapor Retarder Required

ASTM C 1136, Type I, maximum moisture vapor transmission 0.02 perms, minimum puncture resistance 50 Beach units on all surfaces except concealed ductwork, where Type II, maximum moisture vapor transmission 0.02 perms, a minimum puncture resistance of 25 Beach units is acceptable.

### 2.1.10   Wire

Soft annealed ASTM A 580/A 580M Type 302, 304 or 316 stainless steel, 16 or 18 gauge.

## 2.2   	PIPE INSULATION MATERIALS

Pipe insulation materials shall be limited to those listed herein and shall meet the following requirements:

### 2.2.1   Aboveground Cold Pipeline

Insulation for minus 5 degrees to plus 16 degrees C for outdoor, shall be as follows:

Mineral Fiber:  ASTM C 547

### 2.2.2   Aboveground Hot Pipeline

Insulation for above 16 degrees C, for outdoor, indoor, exposed or concealed applications shall meet the following requirements.  Supply the insulation with manufacturers recommended factory applied jacket.

a.  	Mineral Fiber: ASTM C 547, Types I, II or III, supply the insulation with manufacturers recommended factory applied jacket.

## 2.3  	DUCT INSULATION MATERIALS

Duct insulation materials shall be limited to those listed herein and shall meet the following requirements:

### 2.3.1   Rigid Mineral Fiber: ASTM C 612, Type IA, IB, II, III, & IV.

### 2.3.2   Flexible Mineral Fiber: ASTM C 553, Type I, or Type II up to 121 C.  ASTM C 1290

### Type III.

## 2.4   	EQUIPMENT INSULATION MATERIALS

Equipment insulation materials shall be limited to those listed herein and shall meet the following requirements:

### 2.4.1   	Cold Equipment Insulation: For temperatures below 16 degrees C.

#### 2.4.1.1 Cellular Glass: ASTM C 552, Type I, Type III, or Type IV as required.

#### 2.4.1.2 Flexible Cellular Insulation: ASTM C 534, Type II.

#### 2.4.1.3 Phenolic Foam: ASTM C 1126 Type II shall comply with ASTM C 795.

### 2.4.2   	Hot Equipment Insulation: For temperatures above 16 degrees C.

#### 2.4.2.1   Rigid Mineral Fiber

ASTM C 612, Type IA, IB, II, III, IV, or V as required for temperature encountered to 982 degrees C.

#### 2.4.2.2   Flexible Mineral Fiber

ASTM C 553, Type I, II, III, IV, V, VI or VII as required for temperature encountered to 649 degrees C.

#### 2.4.2.3   Cellular Glass: ASTM C 552, Type I, Type III, or Type IV as required.

#### 2.4.2.4   Flexible Cellular Insulation: ASTM C 534, Type II, to 93 degrees C.

#### 2.4.2.5 Phenolic Foam: ASTM C 1126 Type II to 121 degrees C. shall comply with ASTM C 795.

#### 2.4.2.6   Molded Expanded Perlite: ASTM C 610.

# PART 3   EXECUTION

## 3.1   	APPLICATION - GENERAL

### 3.1.1   Installation

Except as otherwise specified, material shall be installed in accordance with the manufacturer's written instructions. Insulation materials shall not be applied until tests specified in other sections of this specification are completed.  Material such as rust, scale, dirt and moisture shall be removed from surfaces to receive insulation. Insulation shall be kept clean and dry. Insulation shall not be removed from its shipping containers until the day it is ready to use and shall be returned to like containers or equally protected from dirt and moisture at the end of each workday. Insulation that becomes dirty shall be thoroughly cleaned prior to use.  If insulation becomes wet or if cleaning does not restore the surfaces to like new condition, the insulation will be rejected, and shall be immediately removed from the jobsite. Joints shall be staggered on multi layer insulation. Mineral fiber thermal insulating cement shall be mixed with demineralized water when used on stainless steel surfaces. Insulation, jacketing and accessories shall be installed in accordance with MICA Insulation Stds standard plates except where modified herein or on the drawings.

### 3.1.2   	Fire stopping

Where pipes and ducts pass through firewalls, fire partitions, above grade floors, and fire rated chase walls, the penetration shall be sealed with fire stopping materials of the same rating.

### 3.1.3   	Painting and Finishing: Painting shall be as specified in relevant Sections.

### 3.1.4   	Installation of Flexible Cellular Insulation

Flexible cellular insulation shall be installed with seams and joints sealed with a contact adhesive. Flexible cellular insulation shall not be used on surfaces greater than 93 degrees C. Seams shall be staggered when applying multiple layers of insulation. Insulation exposed to weather and not shown to have jacketing shall be protected with two coats of UV resistant finish as recommended by the manufacturer after the adhesive is dry.

### 3.1.5   	Welding

No welding shall be done on piping, duct or equipment without written approval of the Engineer. The capacitor discharge welding process may be used for securing metal fasteners to duct.

### 3.1.6   	Pipes/Ducts/Equipment which Require Insulation

Insulation is required on all pipes, ducts, or equipment, except for omitted items, as specified.

## 3.2   	PIPE INSULATION INSTALLATION

### 3.2.1   Pipe Insulation

#### 3.2.1.1   General

Pipe insulation shall be installed on aboveground hot & cold pipeline systems as specified below to form a continuous thermal retarder, including straight runs, fittings & appurtenances unless specified otherwise. Installation shall be with full length units of insulation & using a single cut piece to complete a run. Cut pieces or scraps abutting each other shall not be used. Pipe insulation shall be omitted on the following:

a.  	Pipe used solely for fire protection.

b.  	Chromium plated pipe to plumbing fixtures. However, fixtures for use by the physically handicapped shall have the hot water supply and drain, including the trap, insulated where exposed.

c.  	Sanitary drain lines.

d.  	Heating pipes in heated spaces.

e.  	Domestic Cold water pipes, indoors.

f.  	Interior roof drains, where condensate is not expected.

#### 3.2.1.2 Pipes Passing Through Walls, Roofs, and Floors

a.  	Pipe insulation shall be continuous through the sleeve.

b.  	An aluminum jacket with factory applied moisture retarder shall be provided over the insulation wherever penetrations require sealing.

c.  	Where penetrating interior walls, the aluminum jacket shall extend 50mm beyond either side of the wall and shall be secured on each end with a band.

d.  	Where penetrating floors, the aluminum jacket shall extend from a point below the backup material to a point 250 mm above the floor with one band at the floor and one not more than 25 mm from the end of the aluminum jacket.

e.  	Where penetrating waterproofed floors, the aluminum jacket shall extend from below the backup material to a point 50mm above the flashing with a band 25mm from the end of the aluminum jacket.

f.  	Where penetrating exterior walls, the aluminum jacket required for pipe exposed to weather shall continue through the sleeve to a point 50 mm beyond the interior surface of the wall.

g.  	Where penetrating roofs, pipe shall be insulated as required for interior service to a point flush with the top of the flashing and sealed with vapor retarder coating. The insulation for exterior application shall butt tightly to the top of flashing and interior insulation. The exterior aluminum jacket shall extend 50mm down beyond the end of the insulation to form a counter flashing. The flashing and counter flashing shall be sealed underneath with caulking.

h.  	For hot water pipes supplying lavatories or other similar heated service, which requires insulation, the insulation shall be terminated on the backside of the finished wall. The insulation termination shall be protected with two coats of vapor barrier coating with a minimum total thickness of 2.0mm applied with glass tape embedded between coats (if applicable). The coating shall extend out onto the insulation 50.0mm & shall seal the end of the insulation. Glass tape seams shall overlap 25mm. Caulk the annular space between the pipe & wall penetration with approved fire stop material. Cover the pipe & wall penetration with a properly sized (well fitting) escutcheon plate. The escutcheon plate shall overlap the wall penetration at least 10mm.

#### 3.2.1.3   Pipes Passing Through Hangers

a.  	Insulation, whether hot or cold application, shall be continuous through hangers. All horizontal pipes 50mm and smaller shall be supported on hangers with the addition of a Type 40 protection shield to protect the insulation in accordance with MSS SP-69.  Whenever insulation shows signs of being compressed, or when the insulation or jacket shows visible signs of distortion at or near the support shield, insulation inserts as specified below for piping larger than 50 mm shall be installed.

b.  	Horizontal pipes larger than 50mm at 16 degrees C and above shall be supported on hangers in accordance with MSS SP-69, and relevant Section.

c.  	Horizontal pipes larger than 50 mm and below 16 degrees C shall be supported on hangers with the addition of a Type 40 protection shield in accordance with MSS SP-69. An insulation insert of cellular glass or calcium silicate shall be installed above each shield. The insert shall cover not less than the bottom 180 degree arc of the pipe. Inserts shall be the same thickness as the insulation, and shall extend 50mm on each end beyond the protection shield. When insulation inserts are required per the above, and the insulation thickness is less than 25mm, wooden or cork dowels or blocks may be installed between the pipe and the shield to prevent the weight of the pipe from crushing the insulation, as an option to installing insulation inserts. The insulation jacket shall be continuous over the wooden dowel, wooden block, or insulation insert.

d.  	Vertical pipes shall be supported with either Type 8 or Type 42 riser clamps with the addition of two Type 40 protection shields in accordance with MSS SP-69 covering the 360 degree arc of the insulation. An insulation insert of cellular glass or calcium silicate shall be installed between each shield and the pipe. The insert shall cover the 360 degree arc of the pipe. Inserts shall be the same thickness as the insulation, and shall extend 50mm on each end beyond the protection shield. When insulation inserts are required per the above, and the insulation thickness is less than 25mm, wooden or cork dowels or blocks may be installed between the pipe and the shield to prevent the hanger from crushing the insulation, as an option instead of installing insulation inserts. The insulation jacket shall be continuous over the wooden dowel, wooden block, or insulation insert. The vertical weight of the pipe shall be supported with hangers located in a horizontal section of the pipe. When the pipe riser is longer than 9m, the weight of the pipe shall be additionally supported with hangers in the vertical run of the pipe, which are directly clamped to the pipe, penetrating the pipe insulation.  These hangers shall be insulated and the insulation jacket sealed as indicated herein for anchors in a similar service.

e.  	Inserts shall be covered with a jacket material of the same appearance and quality as the adjoining pipe insulation jacket, shall overlap the adjoining pipe jacket 38mm, and shall be sealed as required for the pipe jacket. The jacket material used to cover inserts in flexible cellular insulation shall conform to ASTM C 1136, Type 1, and is allowed to be of a different material than the adjoining insulation material.

#### 3.2.1.4   Flexible Cellular Pipe Insulation

Flexible cellular pipe insulation shall be tubular form for pipe sizes 150 mm & less. Type II sheet insulation used on pipes larger than 150mm shall not be stretched around the pipe. On pipes larger than 300mm, adhere insulation directly to the pipe on the lower 1/3 of the pipe. Seams shall be staggered when applying multiple layers of insulation. Sweat fittings shall be insulated with miter-cut pieces the same size as on adjacent piping. Screwed fittings shall be insulated with sleeved fitting covers fabricated from miter-cut pieces and shall be overlapped and sealed to the adjacent pipe insulation.

#### 3.2.1.5   Pipes in high abuse areas.

In high abuse areas such as janitor closets and traffic areas in equipment rooms, kitchens, and mechanical rooms, aluminum jackets shall be utilized.  Pipe insulation to the 1.8 m level shall be protected.

### 3.2.2   Aboveground Cold Pipelines

The following cold pipelines shall be insulated per Table I minus 5 degrees C to plus 16 degrees C:

a.  	Domestic cold water, outdoors.

#### 3.2.2.1   Insulation Thickness

Insulation thickness for cold pipelines shall be determined using Table I.

Table I - Cold Piping Insulation Thickness Pipe Size (mm)

Run outs   25 mm     30       	65 -      125 -   205 mm

Type of  up to & 50 mm    100 mm    150 mm &

Service Type  	50 mm* less  larger

Cold domestic  MF      	15      		25       25        	40        40       40

Water

LEGEND:

MF - Mineral Fiber

#### 3.2.2.2 Jacket for Mineral Fiber, Cellular Glass and Phenolic Foam Insulated Pipe

Insulation shall be covered with a factory applied vapor retarder jacket or field applied seal welded PVC jacket. Insulation inside the building shown to be protected with an aluminum jacket shall have the insulation and vapor retarder jacket installed as specified herein. The aluminum jacket shall be installed as specified for piping exposed to weather, except sealing of the laps of the aluminum jacket is not required. In high abuse areas such as janitor closets and traffic areas in equipment rooms, kitchens, and mechanical rooms, aluminum jackets shall be utilized. Pipe insulation to the 1.8 m level will be protected.

#### 3.2.2.3 Insulation for Straight Runs (Mineral Fiber, Cellular Glass & Phenolic Foam)

a.  	Insulation shall be applied to the pipe with joints tightly butted.  All butted joints & ends shall be sealed with a vapor retarder coating.

b.  	Longitudinal laps of the jacket material shall overlap not less than 38mm. Butt strips 75mm wide shall be provided for circumferential joints.

c.  	Laps & butt strips shall be secured with adhesive and stapled on 100mm centers if not factory self-sealing. If staples are used, they shall be sealed per paragraph 3.2.2.3 e.

d.  	All Staples, including those used to repair factory self-seal lap systems, shall be coated with a vapor retarder coating. All seams, except those on factory self-seal systems shall be coated with vapor retarder coating.

e.  	Breaks & punctures in the jacket material shall be patched by wrapping a strip of jacket material around the pipe and securing it with adhesive, stapling, & coating with vapor retarder coating. The patch shall extend not less than 38 mm past the break.

f.  	At penetrations such as thermometers, the voids in the insulation shall be filled and sealed with vapor retarder coating.

#### 3.2.2.4   Insulation for Fittings and Accessories

a.  	Pipe insulation shall be tightly butted to the insulation of the fittings and accessories. The butted joints and ends shall be coated with vapor retarder coating.

b.  	Precut or preformed insulation shall be placed around all fittings & accessories & shall conform to MICA plates except as modified herein:5 for anchors; 10, 11, & 13 for fittings;14 for valves; & 17 for flanges & unions. Insulation shall be the same insulation as the pipe insulation, including same density, thickness, & thermal conductivity. Where precut/preformed is unavailable, rigid preformed pipe insulation sections may be segmented into the shape required. Insulation of the same thickness & conductivity as the adjoining pipe insulation shall be used. If nesting size insulation is used, the insulation shall be overlapped 50 mm or one pipe diameter. Elbows insulated using segments shall conform to MICA Tables 12.20 "Mitered Insulation Elbow'.

c.  	Upon completion of insulation installation on flanges, unions, valves, anchors, fittings & accessories, terminations, seams, joints & insulation not protected by factory vapor retarder jackets or PVC fitting covers shall be protected with two coats of vapor retarder coating with a minimum total thickness of 2.0 mm, applied with glass tape embedded between coats. Tape seams shall overlap 25mm. The coating shall extend out onto the adjoining pipe insulation 50mm. Fabricated insulation with a factory vapor retarder jacket shall be protected with two coats of vapor retarder coating with a minimum thickness of 2 mm and with a 50mm wide glass tape embedded between coats.  Where fitting insulation butts to pipe insulation, the joints shall be sealed with a vapor retarder coating and a 100mm wide ASJ tape, which matches the jacket of the pipe insulation.

d.  	Anchors attached directly to the pipe shall be insulated for a sufficient distance to prevent condensation but not less than 150 mm from the insulation surface.

e.  	Insulation shall be marked showing the location of unions, strainers, and check valves.

### 3.2.3   	Aboveground Hot Pipelines

The following hot pipelines above 16 degrees C shall be insulated per Table II:

a.  Domestic hot water supply & recirculating system.

b.  Steam.

#### 3.2.3.1   Insulation Thickness

Insulation thickness for hot pipelines shall be determined using Table II.

Table II - Hot Piping Insulation Thickness Pipe Size (mm)

Type of                	Run outs   	25 mm 	32 -    65 -    125 -   205 mm

Service                	up to       	&       	50      100     150      &

(degrees C)     	Type   	50 mm*     	less      mm      mm      mm    larger

Hot domestic

water supply&

recirculating

system 		MF   	15        		40        40      40      40      40

(93C max)**

High Temp Hot

water & steam,	MF   	40        		80         90     100     100    115

(177C-260C)

*  	When run outs to terminal units exceed 3.66 m, the entire length of run out shall be insulated like the main feed pipe.

**  	Applied to recirculating sections of service or domestic hot water systems and first 2.4 meters from storage tank for non-recirculating systems.

LEGEND:

MF - Mineral Fiber

Insulation shall be covered, in accordance with manufacturer's recommendations, with a factory applied Type II jacket or field applied aluminum where required or seal welded PVC.

#### 3.2.3.3   Insulation for Straight Runs

a.  	Insulation shall be applied to the pipe with joints tightly butted.

b.  	Longitudinal laps of the jacket material shall overlap not less than 38mm, and butt strips75 mm wide shall be provided for circumferential joints.

c.  	Laps and butt strips shall be secured with adhesive and stapled on 100 mm centers if not factory self-sealing.  Adhesive may be omitted where pipe is concealed.

d.  	Factory self-sealing lap systems may be used when the ambient temperature is between 4 degrees & 49 degrees C & shall be installed in accordance with manufacturer's instructions. Laps & butt strips shall be stapled whenever there is non adhesion of the system. Where gaps occur, the section shall be replaced or the gap repaired by applying adhesive under the lap & then stapling.

e.  	Breaks and punctures in the jacket material shall be patched by either wrapping a strip of jacket material around the pipe and securing with adhesive and staple on 100mm centers (if not factory self-sealing), or patching with tape and sealing with a brush coat of vapor retarder coating. Adhesive may be omitted where pipe is concealed. Patch shall extend not less than 38mm past the break.

f.  	Flexible cellular pipe insulation shall be installed by slitting tubular sections and applying onto piping or tubing. Alternately, whenever possible, slide unslit sections over the open ends of piping or tubing. All seams and butt joints shall be secured and sealed with adhesive. When using self seal products only the butt joints shall be secured with adhesive. Insulation shall be pushed on the pipe, never pulled. Stretching of insulation may result in open seams and joints. All edges shall be clean cut.  Rough or jagged edges of the insulation shall not be permitted.  Proper tools such as sharp knives shall be used. Type II sheet insulation when used on pipe larger than 150mm shall not be stretched around the pipe. On pipes larger than 300mm, adhere sheet insulation directly to the pipe on the lower 1/3 of the pipe.

#### 3.2.3.4   Insulation for Fittings and Accessories

a.  	Pipe insulation shall be tightly butted to the insulation of the fittings and accessories.

b.  	Precut or preformed insulation shall be placed around all fittings and accessories and shall conform to MICA plates, except as modified herein: 5 for anchors; 10, 11, 12,and 13 for fittings; 14, 15 and 16 for valves; 17 for flanges and unions; and 18 for couplings. Insulation shall be the same as the pipe insulation, including same density, thickness, and thermal conductivity.  Where precut/preformed is unavailable, rigid preformed pipe insulation sections may be segmented into the shape required.  Insulation of the same thickness and conductivity as the adjoining pipe insulation shall be used.  If nesting size insulation is used, the insulation shall be overlapped 50mm or one pipe diameter. Elbows insulated using segments shall conform to MICA Tables 12.20 "Mitered Insulation Elbow".

c.  	Upon completion of installation of insulation on flanges, unions, valves, anchors, fittings and accessories, terminations and insulation not protected by factory vapor retarder jackets or PVC fitting covers shall be protected with two coats of adhesive applied with glass tape embedded between coats. Tape seams shall overlap 25mm. Adhesive shall extend onto the adjoining insulation not less than 50mm. The total dry film thickness shall be not less than 2.0 mm.

d.  	Insulation terminations shall be tapered to unions at a 45-degree angle.

e.  	At the option of the Contractor, factory premolded one- or two-piece PVC fitting covers may be used in lieu of the adhesive and embedded glass tape. Factory premolded segments or factory or field cut blanket insert insulation segments shall be used under the cover and shall be the same thickness as adjoining pipe insulation. The covers shall be secured by PVC vapor retarder tape, adhesive, seal-welding or with tacks made for securing PVC covers.

### 3.2.4   	Piping Exposed to Weather

Piping exposed to weather shall be insulated and jacketed as specified for the applicable service inside the building. After this procedure, an aluminum jacket or PVC jacket shall be applied. PVC jacketing requires no factory applied jacket beneath it, however an all service jacket shall be applied if factory applied jacketing is not furnished. Flexible cellular insulation exposed to weather shall be treated in accordance with paragraph INSTALLATION OF FLEXIBLE CELLULAR INSULATION.

#### 3.2.4.1   Aluminum Jacket

The jacket for hot piping may be factory applied. The jacket shall overlap not less than 50mm at longitudinal and circumferential joints and shall be secured with bands at not more than 300mm centers. Longitudinal joints shall be overlapped down to shed water and located at 4 or 8 o'clock positions. Joints on piping 16 degrees C and below shall be sealed with caulking while overlapping to prevent moisture penetration.  Where jacketing on piping 16 degrees C and below abuts an uninsulated surface, joints shall be caulked to prevent moisture penetration. Joints on piping above 16 degrees C shall be sealed with a moisture retarder.

#### 3.2.4.2   Insulation for Fittings

Flanges, unions, valves, fittings, and accessories shall be insulated and finished as specified for the applicable service. Two coats of breather emulsion type weatherproof mastic (impermeable to water, permeable to air) recommended by the insulation manufacturer shall be applied with glass tape embedded between coats. Tape overlaps shall be not less than 25mm and the adjoining aluminum jacket not less than 50mm.  Factory preformed aluminum jackets may be used in lieu of the above.  Molded PVC fitting covers shall be provided when PVC jackets are used for straight runs of pipe. PVC fitting covers shall have adhesive welded joints and shall be weatherproof.

#### 3.2.4.3   PVC Jacket

PVC jacket shall be ultraviolet resistant and adhesive welded weather tight with manufacturer's recommended adhesive. Installation shall include provision for thermal expansion.

### 3.2.5  	Below ground Pipe Insulation

The following shall be included:

a.  Heating hot water.

#### 3.2.5.1   Type of Insulation

Below ground pipe shall be insulated with 75mm cellular glass insulation set in a coat of bedding compound as recommended by the manufacturer.

#### 3.2.5.2   Installation of Below ground Pipe Insulation

a.  	Bore surfaces of the insulation shall be coated with a thin coat of gypsum cement of a type recommended by the insulation manufacturer. Coating thickness shall be sufficient to fill surface cells of insulation. Mastic type materials shall not be used for this coating.

b.  	Stainless steel bands, 19mm wide by 0.5080mm thick shall be used to secure insulation in place. A minimum of two bands per section of insulation shall be applied. As an alternate, fiberglass reinforced tape may be used to secure insulation on piping up to 300mm in diameter. A minimum of two bands per section of insulation shall be applied.

c.  	Insulation shall terminate at anchor blocks but shall be continuous through sleeves and manholes.

d.  	At point of entry to buildings, underground insulation shall be terminated 50 mm inside the wall or floor, shall butt tightly against the aboveground insulation and the butt joint shall be sealed with high temperature silicone sealant.

e.  	Provision for expansion and contraction shall be made in accordance with the insulation manufacturer's recommendations.

f.  	Flanges, couplings, valves, and fittings shall be insulated with factory premolded, prefabricated, or field-fabricated sections of insulation of the same material and thickness as the adjoining pipe insulation. Insulation sections shall be secured in place with wire, bore surfaces coated, and joints sealed as specified.

g.  	Insulation, including fittings, shall be finished with three coats of asphaltic mastic, with 6 by 5.5 mesh synthetic reinforcing fabric embedded between coats. Fabric shall be overlapped a minimum of 50mm at joints. Total film thickness shall be a minimum of 4.7 mm. As an alternate, a prefabricated bituminous laminated jacket, reinforced with internal reinforcement mesh, shall be applied to the insulation. Jacketing material and application procedures shall match manufacturer's written instructions.

h.   	At termination points, other than building entrances, the mastic and cloth or tape shall cover the ends of insulation and extend 50 mm along the bare pipe.

## 3.3   	DUCT INSULATION INSTALLATION

Except for oven hood exhaust duct insulation, corner angles shall be installed on external corners of insulation on ductwork in exposed finished spaces before covering with jacket. Air conditioned spaces shall be defined as those spaces directly supplied with cooled conditioned air (or provided with a cooling device such as a fan-coil unit) and heated conditioned air (or provided with a heating device such as a unit heater, radiator or convector).

### 3.3.1   	Duct Insulation Thickness

Duct insulation thickness shall be in accordance with the following:

Conditioned Spaces:

Cold & Warm Air Ducts                        	40

Relief & Fresh Air Ducts    	         	25

Exhaust Air Ducts                       	25

Un-conditioned Spaces:

Cold & Warm Air Ducts         	  	50

Relief & Fresh Air Ducts                       	40

Exhaust Air Ducts                              	40

Outdoor / Weather Exposed:

Cold & Warm Air Ducts                       	75

Relief & Fresh Air Ducts                       	50

Exhaust Air Ducts                              	50

### 3.3.2   	Insulation and Vapor Retarder for Dual Air Ducts (Cold & Warm)

Insulation and vapor retarder shall be provided for the following cold & warm air ducts and associated equipment.

a.  	Supply ducts.

b.  	Return air ducts.

c.  	Relief ducts.

d.  	Flexible run outs (field-insulated).

e.  	Plenums.

f.  	Duct-mounted coil casings.

g.  	Coil headers and return bends.

h.  	Coil casings.

i.  	Fresh air intake ducts.

j.  	Filter boxes.

k.  	Mixing boxes (field-insulated).

l.  	Supply fans (field-insulated).

m.  	Site-erected air conditioner casings.

n.  	Ducts exposed to weather.

o.  	Combustion air intake ducts.

Insulation for rectangular ducts shall be flexible type where concealed, minimum density 24 kg per cubic meter and rigid type where exposed, minimum density 64 kg per cubic meter. Insulation for round/oval ducts shall be flexible type, minimum density 24 kg per cubic meter with a factory Type I or II jacket; or, a semi rigid board, minimum density 64 kg per cubic meter, formed or fabricated to a tight fit, edges beveled and joints tightly butted and staggered, with a factory applied Type I or II all service jacket. Insulation for exposed ducts shall be provided with either a white, paintable, factory-applied Type I jacket or a vapor retarder jacket coating finish as specified. Insulation on concealed duct shall be provided with a factory-applied Type I or II vapor retarder jacket. The total dry film thickness shall be approximately 2.0mm. Duct insulation shall be continuous through sleeves and prepared openings except firewall penetrations.  Duct insulation terminating at fire dampers, shall be continuous over the damper collar and retaining angle of fire dampers, which are exposed to unconditioned air and which may be prone to condensate formation. Duct insulation and vapor retarder shall cover the collar, neck, and any uninsulated surfaces of diffusers, registers and grills.  Vapor retarder materials shall be applied to form a complete unbroken vapor seal over the insulation. Sheet Metal Duct shall be sealed in accordance with relevant sections.

#### 3.3.2.1   Installation on Concealed Duct

a.  	For rectangular, oval or round ducts, insulation shall be attached by applying adhesive around the entire perimeter of the duct in 150mm wide strips on 300 mm centers.

b.  	For rectangular and oval ducts, 600 mm (24 inches) and larger insulation shall be additionally secured to bottom of ducts by the use of mechanical fasteners. Fasteners shall be spaced on 400 mm centers and not more than 400 mm from duct corners.

c.  	For rectangular, oval and round ducts, mechanical fasteners shall be provided on sides of duct risers for all duct sizes.  Fasteners shall be spaced on 400 mm centers and not more than 400 mm from duct corners.

d.  	Insulation shall be impaled on the mechanical fasteners (self stick pins) where used and shall be pressed thoroughly into the adhesive. Care shall be taken to ensure vapor retarder jacket joints overlap 50 mm.  The insulation shall not be compressed to a thickness less than that specified. Insulation shall be carried over standing seams and trapeze-type duct hangers.

e.  	Self-locking washers shall be installed where mechanical fasteners are used. The pin shall be trimmed back & bent over.

f.  	Jacket overlaps shall be secured with staples and tape as necessary to ensure a secure seal. Staples, tape and seams shall be coated with a brush coat of vapor retarder coating.

g.  	Breaks in the jacket material shall be covered with patches of the same material as the vapor retarder jacket. The patches shall extend not less than 50mm beyond the break or penetration in all directions and shall be secured with tape and staples. Staples and tape joints shall be sealed with a brush coat of vapor retarder coating.

h.  	At jacket penetrations such as hangers, thermometers, & damper operating rods, voids in the insulation shall be filled& the penetration sealed with a brush coat of vapor retarder coating.

i.  	Insulation terminations and pin punctures shall be sealed and flashed with a reinforced vapor retarder coating finish or tape with a brush coat of vapor retarder coating. The coating shall overlap the adjoining insulation and uninsulated surface 50mm.  Pin puncture coatings shall extend 50mm from the puncture in all directions.

j.  	Where insulation standoff brackets occur, insulation shall be extended under the bracket and the jacket terminated at the bracket.

#### 3.3.2.2   Installation on Exposed Duct Work

a.  	For rectangular ducts, rigid insulation shall be secured to the duct by mechanical fasteners on all four sides of the duct, spaced not more than 300mm apart and not more than 75mm from the edges of the insulation joints. A minimum of two rows of fasteners shall be provided for each side of duct 300mm and larger. One row shall be provided for each side of duct less than 300mm.

b.  	Duct insulation shall be formed with minimum jacket seams.  Each piece of rigid insulation shall be fastened to the duct using mechanical fasteners. When the height of projections is less than the insulation thickness, insulation shall be brought up to standing seams, reinforcing, and other vertical projections and shall not be carried over. Vapor retarder jacket shall be continuous across seams, reinforcing, and projections. When height of projections is greater than the insulation thickness, insulation and jacket shall be carried over.

c.  	Insulation shall be impaled on the fasteners; self-locking washers shall be installed and the pin trimmed or bent over.

d.  	Joints in the insulation jacket shall be sealed with a 100mm wide strip of tape. Tape seams shall be sealed with a brush coat of vapor retarder coating.

e.  	Breaks and ribs or standing seam penetrations in the jacket material shall be covered with a patch of the same material as the jacket.  Patches shall extend not less than 50 mm beyond the break or penetration and shall be secured with tape and stapled. Staples and joints shall be sealed with a brush coat of vapor retarder coating.

f.  	At jacket penetrations such as hangers, thermometers, and damper operating rods, the voids in the insulation shall be filled and the penetrations sealed with a brush coat of vapor retarder coating.

g.  	Insulation terminations and pin punctures shall be sealed and flashed with a reinforced vapor retarder coating finish. The coating shall overlap the adjoining insulation and uninsulated surface 50mm. Pin puncture coatings shall extend 50mm from the puncture in all directions.

h.  	Oval and round ducts, flexible type, shall be insulated with factory Type I jacket insulation with minimum density of 48 kg per cubic meter, attached as per MICA standards.

### 3.3.3   	Duct Test Holes

After duct systems have been tested, adjusted, and balanced, breaks in the insulation and jacket shall be repaired in accordance with the applicable section of this specification for the type of duct insulation to be repaired.

### 3.3.4   	Duct Exposed to Weather

#### 3.3.4.1   Installation

Ducts exposed to weather shall be insulated and finished as specified for the applicable service for exposed duct inside the building. After the above is accomplished, the insulation shall then be further finished as detailed in the following subparagraphs.

#### 3.3.4.2   Round Duct

Aluminum jacket with factory applied moisture retarder shall be applied with the joints lapped not less than 75mm and secured with bands located at circumferential laps and at not more than 300mm intervals throughout.  Horizontal joints shall lap down to shed water and located at 4 or 8 o'clock position.  Joints shall be sealed with caulking to prevent moisture penetration. Where jacketing abuts an uninsulated surface, joints shall be sealed with caulking.

#### 3.3.4.3   Fittings

Fittings and other irregular shapes shall be finished as specified for rectangular ducts.

#### 3.3.4.4 Rectangular Ducts

Two coats of weather barrier mastic reinforced with fabric or mesh for outdoor application shall be applied to the entire surface. Each coat of weatherproof mastic shall be 2.0 mm minimum thickness. The exterior shall be a metal jacketing applied for mechanical abuse and weather protection, and secured with screws.

#### 3.3.4.5   Ducts in Mechanical Rooms

Ducts in mechanical rooms shall be insulated with minimum 75 mm thick Rigid Mineral Fiber of 160 kg/cubic meter density and finished as specified for the weather exposed ducts.

## 3.4   	EQUIPMENT INSULATION INSTALLATION

### 3.4.1   General

Removable insulation sections shall be provided to cover parts of equipment, which must be opened periodically for maintenance including vessel covers, fasteners, flanges and accessories.  Equipment insulation shall be omitted on the following:

a.  	Handholes.

b.  	Boiler manholes.

c.  	Cleanouts.

d.  	ASME stamps.

e.  	Manufacturer's nameplates.

### 3.4.2   Insulation for Cold Equipment

Cold equipment below 16 degrees C:  Insulation shall be furnished on equipment handling media below 16 degrees C including the following:

a.  	Pumps.

b.  	Refrigeration equipment parts that are not factory insulated.

c.  	Drip pans under chilled equipment.

d.  	Cold and chilled water pumps.

e.  	Roof drain bodies.

f.  	Air handling equipment parts that are not factory insulated.

g.  	Expansion and air separation tanks.

#### 3.4.2.1   Insulation Type

Insulation shall be suitable for the temperature encountered.  Thicknesses shall be as follows:

a.  	Equipment handling media between 2 and 16 degrees C: 40 mm (1.5 inch) thick cellular glass, 25 mm thick flexible cellular, 25 mm thick phenolic foam.

b.  	Equipment handling media between minus 18 degrees C and plus 1 degrees C: 75 mm (3 inch) thick cellular glass, 40 mm flexible cellular, 40 mm thick phenolic foam.

#### 3.4.2.2   Pump Insulation

a.  	Pumps shall be insulated by forming a box around the pump housing. The box shall be constructed by forming the bottom and sides using joints, which do not leave raw ends of insulation exposed. Joints between sides and between sides and bottom shall be joined by adhesive with lap strips for rigid mineral fiber and contact adhesive for flexible cellular insulation. The box shall conform to the requirements of MICA Insulation Stds plate No. 49 when using flexible cellular insulation. Joints between top cover and sides shall fit tightly forming a female shiplap joint on the side pieces and a male joint on the top cover, thus making the top cover removable.

b.  	Exposed insulation corners shall be protected with corner angles.

c.  	Upon completion of installation of the insulation, including removable sections, two coats of vapor retarder coating shall be applied with a layer of glass cloth embedded between the coats.  The total dry thickness of the finish shall be 2.0mm. A parting line shall be provided between the box and the removable sections allowing the removable sections to be removed without disturbing the insulation coating. Caulking shall be applied to parting line, between equipment and removable section insulation, and at all penetrations.

#### 3.4.2.3   Other Equipment

a.  	Insulation shall be formed or fabricated to fit the equipment. To ensure a tight fit on round equipment, edges shall be beveled and joints shall be tightly butted and staggered.

b.  	Insulation shall be secured in place with bands or wires at intervals as recommended by the manufacturer but not more than 300mm centers except flexible cellular, which shall be adhered. Insulation corners shall be protected under wires and bands with suitable corner angles.

c.  	Cellular glass and phenolic foam insulation shall be set in a coating of bedding compound, and joints shall be sealed with bedding compound as recommended by the manufacturer.

d.  	Insulation on heads of heat exchangers shall be removable.  Removable section joints shall be fabricated using a male-female shiplap type joint. The entire surface of the removable section shall be finished by applying two coats of vapor retarder coating with a layer of glass cloth embedded between the coats. The total dry thickness of the finish shall be 2.0 mm.

e.  	Exposed insulation corners shall be protected with corner angles.

f.  	Insulation on equipment with ribs shall be applied over 150x150mm by 12 gauge welded wire fabric, which has been cinched in place, or if approved by the Engineer, spot welded to the equipment over the ribs. Insulation shall be secured to the fabric with J-hooks and 50x50mm washers or shall be securely banded or wired in place on 300 mm centers.

#### 3.4.2.4   Vapor Retarder

Upon completion of installation of insulation, penetrations shall be caulked. Two coats of vapor retarder coating shall be applied over insulation, including removable sections, with a layer of open mesh synthetic fabric embedded between the coats. The total dry thickness of the finish shall be 2.0mm. Caulking shall be applied to parting line between equipment and removable section insulation.

### 3.4.3   Insulation for Hot Equipment

Insulation shall be furnished on equipment handling media above 16 degrees C including the following:

a.  	Hot water generators.

b.  	Pumps handling media above 54 degrees C.

c.  	Buffer tank.

d.  	Flash tanks.

e.  	Feed Water Heaters.

f.  	Unjacketed boilers or parts of boilers.

g.  	Boiler flue gas connection from boiler to stack.

h.  	Fly ash and soot collectors.

i.  	Condensate receivers.

#### 3.4.3.1   Insulation

Insulation shall be suitable for the temperature encountered. Shell and tube-type heat exchangers shall be insulated for the temperature of the shell medium.

Insulation thickness for hot equipment shall be determined using Table IV:

Legend

RMF:  Rigid Mineral Fiber

FMF: Flexible Mineral Fiber

CS: Calcium Silicate

PL: Perlite

CG: Cellular Glass

FC: Flexible Cellular

PF: Phenolic Foam

PC: Polyisocyanurate Foam

TABLE IV Insulation Thickness for Hot Equipment (mm)

Equipment handling steam or other media        	Material 	    Thickness

to indicated pressure or temperature limit

_________________________________________________________________

103.4 kPa	                           		RMF                    	50 mm

or	            	                 		FMF                    	50 mm

121 C                            	     		CS/PL                 	100mm

CG                     	75 mm

PF                     	40 mm

FC (<93 C)		25 mm

PC 			25mm

_________________________________________________________________

1379.0kPa	                           RMF                    	75 mm

or  	            	               FMF                    	75 mm

204 C                                	  CS/PL 		            100 mm

CG   		            100 mm

_________________________________________________________________

316 C                                  	RMF                 	125 mm

FMF                   	150 mm

CS/PL                 	150 mm

CG 		            150 mm

_________________________________________________________________

316 C: Thickness necessary to limit the external temperature of the insulation to 50C, except that diesel engine exhaust piping & mufflers shall be covered with 150mm thick material suitable for 650 degrees C service.  Heat transfer calculations shall be submitted to substantiate insulation & thickness selection.

#### 3.4.3.2   Insulation of Pumps

Pumps shall be insulated by forming a box around the pump housing.  The box shall be constructed by forming the bottom & sides using joints, which do not leave raw ends of insulation exposed. Bottom & sides shall be banded to form a rigid housing, which does not rest on the pump. Joints between top cover &sides shall fit tightly. The top cover shall have a joint forming a female shiplap joint on the side pieces & a male joint on the top cover, making the top cover removable. Two coats of Class I adhesive shall be applied over insulation, including removable sections, with a layer of glass cloth embedded between the coats. A parting line shall be provided between the box & the removable sections allowing the removable sections to be removed without disturbing the insulation coating. The total dry thickness of the finish shall be 2.0mm. Caulking shall be applied to parting line of the removable sections & penetrations.

#### 3.4.3.3   Other Equipment

a.  	Insulation shall be formed or fabricated to fit the equipment.  To ensure a tight fit on round equipment, edges shall be beveled & joints shall be tightly butted and staggered.

b.  	Insulation shall be secured in place with bands or wires at intervals as recommended by the manufacturer but not greater than 300mm centers except flexible cellular, which shall be adhered. Insulation corners shall be protected under wires and bands with suitable corner angles.

c.  	On high vibration equipment, cellular glass insulation shall be set in a coating of bedding compound as recommended by the manufacturer, & joints shall be sealed with bedding compound. Mineral fiber joints shall be filled with finishing cement.

d.  	Insulation on heads of heat exchangers shall be removable. The removable section joint shall be fabricated using a male-female shiplap type joint. Entire surface of the removable section shall be finished as specified.

e.  	Exposed insulation corners shall be protected with corner angles.

f.  	On equipment with ribs, such as boiler flue gas connection, draft fans, & fly ash or soot collectors, insulation shall be applied over 150x150mm by 12 gauge welded wire fabric, which has been cinched in place, or if approved by the Engineer, spot welded to the equipment over the ribs. Insulation shall be secured to the fabric with J-hooks and 50x50mm washers or shall be securely banded or wired in place on 300mm  (maximum) centers.

g.  	On equipment handling media above 316 degrees C, insulation shall be applied in two or more layers with joints staggered.

h.  	Upon completion of installation of insulation, penetrations shall be caulked. Two coats of adhesive shall be applied over insulation, including removable sections, with a layer of glass cloth embedded between the coats. The total dry thickness of the finish shall be 2.0mm. Caulking shall be applied to parting line between equipment and removable section insulation.

### 3.4.4   Equipment Exposed to Weather

#### 3.4.4.1   Installation

Equipment exposed to weather shall be insulated and finished in accordance with the requirements for ducts exposed to weather in paragraph DUCT INSULATION INSTALLATION.

#### 3.4.4.2   Optional Panels

At the option of the Contractor, prefabricated metal insulation panels may be used in lieu of the insulation & finish previously specified.  Thermal performance shall be equal to or better than that specified for field applied insulation.  Panels shall be the standard catalog product of a manufacturer of metal insulation panels. Fastenings, flashing, & support system shall conform to published recommendations of the manufacturer for weatherproof installation & shall prevent moisture from entering the insulation. Panels shall be designed to accommodate thermal expansion & to support a 1112N walking load without permanent deformation or permanent damage to the insulation. Exterior metal cover sheet shall be aluminum and exposed fastenings shall be stainless steel or aluminum.

End Of Section

SECTION:  3.00

MECHANICAL SOUND AND VIBRATION CONTROL

# PART 1   GENERAL

This section applies to all sections of Mechanical Specifications whether referred to, or not.

## 1.1   	DEFINITIONS

### 1.1.1   Decibels dB

Measure of sound level.  Decibels are referenced to either 20 uPa for sound pressure levels or one pW for sound power levels.  dBA is the overall "A" weighted sound level.

### 1.1.2   Machinery

The vibration or noise producing equipment that must be isolated.

### 1.1.3   Manufacturer

The fabricator or contractor of vibration-isolation or seismic-protection materials and equipment.  For mechanical equipment and machinery the term machinery manufacturer will be used.

### 1.1.4   Micropascal uPa

10 to the minus 6 power new tons per square meter.

### 1.1.5   Picowatt pW

10 to the minus 12 power watts.

## 1.2   	SYSTEM DESCRIPTION

### 1.2.1   	Spring Isolator Data

For each type and size of spring isolator, submit the spring outside diameter, deflection, operating spring height, unloaded spring height, solid spring height, the ratio of the outside diameter to the operating spring height, the load to deflection ratio of the springs, and weight and sizes of structural steel members.

### 1.2.2   	Machinery Manufacturer's Sound Data

For each piece of indicated machinery to be vibration isolated, the calculated sound power test data or sound pressure test data as levels in dB in the eight octave bands between 63 and 8,000 Hz.  Refer sound power levels to one pW and sound pressure levels to 20 uPa.  Submit the overall "A" weighted scale sound pressure level in dB.  Submit the standard test procedure used to obtain the sound power or pressure data for the applicable vibration isolation equipment size.

### 1.2.3   	Machinery

For each item of machinery, compare spring static deflections with the specified minimum static deflection, to show that the calculated spring static deflections are not less than the minimum static deflections specified.  Rated spring static deflections are not acceptable in lieu of calculated spring static deflections.  [When seismic protection is required, substantiating calculations are required.]

### 1.2.4   	Machinery Over 136 Kilograms

For machinery items over 136 kg, provide calculations for shear, pull-up, primary overturning, and secondary overturning.

### 1.2.5   	Machinery Vibration Criteria

Provide vibration isolators for mechanical and electrical machinery and associated piping and ductwork, to minimize transmission of vibrations and structure borne noise to the building structure or spaces or from the building structure to the machinery.  Comply with the following vibration schedule.

### 1.2.6   	Machinery Airborne Sound Level Criteria

Air Handling Unit      		94   	90   89   89   89    84    82    79

Make-Up Air Fan      		91   	91   80   84   82    76    71    65

Air Conditioning Unit 	100 	96   90   89   86    80    75    72

Boiler               		75   	72   72   75   76    63    55    50

Chiller              		98 	98   96   95   93    94    88    81

Air Compressor         		90   	89   92  93   92    92    90    81

Pump                   		85   	80   82   82   80    77    74    72

Fan                  		55 	50   48   47   48    46    42    37

#### 1.2.6.1   Basic Criteria

For each piece of machinery in the human work environment, do not exceed the maximum airborne sound levels 84 dB A-weighted scale, continuous or intermittent, or 140 dB peak sound pressure-level, impact or impulse, noise.

# PART 2   PRODUCTS

## 2.1   	CORROSION PROTECTION FOR STEEL PARTS

Hot-dipped galvanized, or equivalent manufacturer standard coatings.  Where steel parts are exposed to the weather, provide galvanized coating of at least 0.61 kg of zinc per square meter of surface.  Coat springs with neoprene.

## 2.2   	NEOPRENE

ASTM D 471 and ASTM D 2240, Grade Duro meter 40, 50, or 60, and oil resistant.

## 2.3   	FLOOR-MOUNTED ISOLATORS

### 2.3.1   Neoprene Isolation Pads

Provide pads at least 6mm thick with cross-ribbed or waffle design.  For concentrated loads, provide steel bearing plates bonded or cold cemented to the pads.

### 2.3.2   Neoprene Isolators

Provide molded neoprene isolators having steel base plates with mounting holes and, at the top, steel mounting plates with mounting holes or threaded inserts.  Provide elements of type and size coded with molded letters or color-coded for capacity identification.  Embed metal parts completely in neoprene.

## 2.4   	SPRING ISOLATORS AND PROTECTED SPRING ISOLATORS

Provide spring isolators or protected spring isolators that are adjustable and laterally stable with free-standing springs of horizontal stiffness at minimum 80 percent of the vertical (axial) stiffness.  For machine-attached and floor-attached restraining elements, separate from metal-to-metal contact by neoprene cushions 3 mm thick minimum.  Provide neoprene acoustic friction pads at least 6 mm thick.

### 2.4.1   Springs

Provide springs with base and compression plates, to keep spring ends parallel during and after deflection to operating height.  Provide outside coil diameters at least 0.8 of the operating height. At operating height, springs shall have additional travel to complete (solid) compression equal to at least 50 percent of the operating deflection.

### 2.4.2   Mounting and Adjustment

Provide base and compression plates with mounting holes or threaded fittings.  Bolt leveling adjustment bolts to machinery or base.

## 2.5   	SUSPENSION ISOLATORS

Provide hangers with suspension isolators encased in open steel brackets. Isolate hanger rods from isolator steel brackets with neoprene-lined opening.

### 2.5.1   Suspension Neoprene Isolators

Provide double-deflection elements with minimum 10 mm deflection.

### 2.5.2   Suspension Spring Isolators

Provide hangers with springs and molded neoprene elements in series. Provide isolators with adjustable spring-preloading devices where required to maintain constant pipe elevations during installation and when pipe operational loads are transferred to the springs.

## 2.6   	MACHINERY BASES

ASTM A 36/A 36M and AISC S342L.

## 2.7   	INERTIA BASES

ASTM A 36/A 36M steel, ASTM C 94 (20 MPa) concrete.

## 2.8   	FLEXIBLE CONNECTORS FOR PIPING

Straight or elbow flexible connectors rated for temperatures, pressures, and fluids to be conveyed.  Provide flexible connectors with the strength 4 times operating pressure at highest system operating temperature. Provide elbow flexible connectors with a permanently set angle.

### 2.8.1   Elastomeric Flexible Connectors

Fabricated of multiple plies of tire cord fabric and elastomeric materials with integral reinforced elastomeric flanges with galvanized malleable iron back up rings.

### 2.8.2   Metal Flexible Connectors

Fabricated of Grade E phosphor bronze, monel or corrugated stainless steel tube covered with comparable bronze or stainless steel braid restraining and pressure cover.

## 2.9   	FLEXIBLE DUCT CONNECTORS

Provide flexible duct connectors fabricated in accordance with SMACNA DCS.

## 2.10   	PIPE GUIDES

Factory-fabricated. Weld steel bar guides to the pipe at a maximum radial spacing of 60 degrees. The outside diameter around the guide bars shall be smaller than the inside diameter of the guide sleeve in accordance with standard field construction practice. For pipe temperatures below 16 degrees C, provide metal sleeve, minimum 16 kg per cubic meter density insulation.

## 2.11   	THRUST RESTRAINTS

Adjustable spring thrust restraints, able to resist the thrust force with at least 25 percent unused capacity. The operating spring deflection shall be not less than 50 percent of the static deflection of the isolation supporting the machinery.

# PART 3   EXECUTION

## 3.1   	INSTALLATION

### 3.1.1   Vibration and Noise Isolation Components

Install vibration-and-noise isolation materials and equipment as indicated and in accordance with machinery manufacturer's instructions.

### 3.1.2   	Suspension Vibration Isolators

Provide suspension isolation hangers for piping, suspended equipment, and suspended equipment platforms in mechanical equipment rooms, as indicated and as specified. For operating load static deflections of 6 mm or less, provide neoprene pads or single deflection neoprene isolators. For operating load static deflections over 8 to 10mm, provide double-deflection neoprene element isolators.  For operating load static deflections over 10 mm, provide isolators with spring and neoprene elements in series.

### 3.1.3   	Vertical Stops

For machinery affected by wind pressure or having an operational weight different from installed weight, provide resilient vertical limit stops which prevent spring extension when weight is removed.  Provide vertical stops for machinery containing liquid, such as water chillers, evaporative coolers, boilers, and cooling towers. Spring isolated or protected spring isolated machinery must rock and move freely within limits of stops or seismic restraint devices.

### 3.1.4   	Thrust Restraints

### Where required, provide pairs of thrust restraints, symmetrically installed on both sides of the steady state line of thrust. 3.1.5   Flexible Pipe and Duct Connectors

Install flexible connectors in accordance with the manufacturer's instructions.  When liquid pulsation dampening is required, flexible connectors with spherical configuration may be used.  Provide restraints for pipe connectors at pumps to prevent connector failure upon pump startup.

### 3.1.6   	Machinery

Provide vibration isolators, flexible connectors in accordance with manufacturer's recommendations.  Machinery with spring isolators or protected spring isolators shall rock or move freely within limits of stops or seismic snubber restraints.

#### 3.1.6.1   Stability

Isolators shall be stable during starting and stopping of machinery without traverse and eccentric movement of machinery that would damage or adversely affect the machinery or attachments.

#### 3.1.6.2 Lateral Motion

The installed vibration isolation system for each piece of floor or ceiling mounted machinery shall have a maximum lateral motion under machinery start up and shut down conditions of not more than 6 mm.  Restrain motions in excess by approved spring mountings.

#### 3.1.6.3 Unbalanced Machinery

Provide foundation suspension systems specifically designed to resist horizontal forces for machinery with large unbalanced horizontal forces. Vibration isolator systems shall conform to the machinery manufacturer's recommendations.

#### 3.1.6.4 Nonrotating Machinery

Mount nonrotating machinery in systems, which includes rotating or vibrating machinery on isolators having the same deflection as the hangers and supports for the pipe connected to.

#### 3.1.6.5 Roof and Upper Floor Mounted Machinery

On the roof or upper floors, mount machinery on isolators with vertical stops.  Rest isolators on beams or structures designed and installed in accordance with the SMACNA Arch. Manual, Plate 61.

### 3.1.7   	Piping and Medium/High Pressure Ductwork

Provide vibration isolation for piping and medium/high pressure ductwork with over 500 Pa water column.  The isolator deflections shall be equal to or greater than the static deflection of the vibration isolators provided for the connected machinery as follows:

#### 3.1.7.1 Medium/High Pressure Ductwork

For a distance of 15 meters from fans, exhausters and blowers.

#### 3.1.7.2 Piping Connected to Vibration Isolated Machinery

For a distance of 15 meters or 50 pipe diameters, whichever is greater.

#### 3.1.7.3 Steam Pressure Reducing Valves

Connected piping for a distance of 15 meters or 50 pipe diameters, whichever is greater.

#### 3.1.7.4   Chilled, Hot, and Dual Temperature Piping

For risers from pumps and for the first 6 meters of the branch connection of the main supply and return piping at each floor.

### 3.1.8   	Water and Steam Distribution Piping Application

Resiliently support piping with combination spring and neoprene isolation hangers. Provide spring elements with 16 mm static deflection; install the hanger with spacing so that the first harmonic natural frequency is not less than 360 Hz.  Provide double-deflection neoprene elements. For the first two isolation hangers from the rotating equipment of 90mm and smaller piping systems, ensure a deflection equal to the equipment-isolation static deflection. For the first four piping isolation hanger supports from rotating equipment of 100mm and larger piping systems, use resilient hanger-rod isolators at a fixed elevation regardless of load changes. Incorporate an adjustable preloading device to transfer the load to the spring element within the hanger mounting after the piping system has been filled with water.

### 3.1.9   Pipe Hanger and Support Installation

#### 3.1.9.1   Pipe Hangers

Provide eye-bolts or swivel joints for pipe hangers to permit pipe thermal or mechanical movement without angular misalignment of hanger vibration isolator.

#### 3.1.9.2   High Temperatures

Where neoprene elements of vibration isolator may be subjected to high pipe temperatures, above 71 degrees C, provide metal heat shields or thermal isolators.

#### 3.1.9.3   Valves

Provide vibration isolation hangers and supports at modulating, pressure reducing, or control valves, which will induce fluid pulsations.  When required or indicated, isolate valves with flexible connectors.

#### 3.1.9.4 Machinery Without Flexible Connections

When piping is not connected to vibrating machinery with flexible connectors, provide the first four hangers with isolation elements designed for deflections equal to equipment vibration isolator deflections (including static, operating, and start-up).

#### 3.1.9.5 Pipe Risers

Provide pipe riser supports with bearing plates and two layers of 6 mm thick ribbed or waffled neoprene pad loaded to not more than 345 kPa.  Separate isolation pads with 6 mm steel plate.  Weld pipe riser clamps at anchor points to the pipe and to pairs of vertical acoustical pipe anchor mountings which shall be rigidly fastened to the steel framing.

#### 3.1.9.6 Supports at Base of Pipe Risers

Piping isolation supports at the base of risers shall be two layers of 13 mm thick heavy-duty neoprene pad separated by 6 mm thick steel plate.  Use bearing plates sized to provide a pad loading of not more than 3447 kPa. Weld the stanchion between the pipe and isolation support to the pipe and weld or bolt to the isolation support. Bolt isolation support to the floor slab with resilient sleeves and washers. Where supplementary steel is required to support piping, provide a maximum deflection of 2 mm at the mid-span of this steel under the load. Rigidly support piping from the supplementary steel with the supplementary steel isolated from the building structure with isolators.

#### 3.1.9.7   Pipe Anchors

Attach each end of the pipe anchor to an omni-directional pipe isolator, which in turn shall be rigidly fastened to the steel framing or structural concrete. Provide a telescoping pipe isolator of two sizes of steel tubing separated by a minimum 13 mm thick pad of heavy-duty neoprene or heavy-duty neoprene and canvas.  Provide vertical restraints by similar material to prevent vertical travel in either direction.  The load on the isolation material shall not exceed 3447 kPa.

### 3.1.10   Medium/High Pressure Ductwork Hanger and Support Installation

Provide ductwork with vibration isolation hangers and supports where required or indicated.  Connect ductwork to equipment with flexible duct connectors.  Segment ductwork with flexible duct connectors.

#### 3.1.10.1   Duct Risers

Provide duct riser supports within shafts with suitable bearing plates and two layers of 6 mm thick ribbed or waffled neoprene pad loaded to not more than 345 kPa.  Separate isolation pads with 6mm steel plate.

#### 3.1.10.2 Supports at Base of Duct Risers

For duct isolation supports at the base of risers, provide two layers of 13 mm thick heavy-duty neoprene pad separated by 6 mm thick steel plate.  Use bearing plates sized to provide a pad loading of not more than 3447 kPa. Weld the stanchion between the duct and isolation support to the pipe, and weld or bolt to the isolation support.  Bolt isolation support to the floor slab with resilient sleeves and washers. Where supplementary steel is required to support ducts, provide a maximum deflection of 6 mm at the midspan of this steel under the supported load.  Rigidly support duct from the supplementary steel and the supplementary steel isolators.

#### 3.1.10.3   Duct Anchors

Attach each end of the duct anchor to an omni-directional isolator, which in turn shall be rigidly fastened to the steel framing or structural concrete as indicated. Vertical restraints shall be provided by similar material arranged to prevent vertical travel in either direction.  The load on the isolation material shall not exceed 3447 kPa.

### 3.1.11   Equipment Room Sound Isolation

Do not allow direct contact between pipe or ducts and walls, floor slabs, roofs, ceilings or partitions of equipment rooms.

#### 3.1.11.1   Pipe Penetrations

Provide galvanized Schedule 40 pipe sleeves and tightly pack annular space between sleeves and pipe with insulation having a flame spread rating not more than 25 and a smoke developed rating not more than 50 when tested in accordance with ASTM E 84, maximum effective temperature 538 degrees C, bulk density 96 kg/cu. meter minimum.  Provide uninsulated pipe with a 25 mm thick mineral fiber sleeve the full length of the penetration and seal each end with an interior or exterior and weather resistant non-hardening compound. Provide sealant and mineral-fiber sleeve of a flame spread rating not more than 25 and a smoke developed rating not more than 50 when tested in accordance with ASTM E 84.

#### 3.1.11.2   Duct Penetrations

Pack openings around ducts with mineral fiber insulation the full length of the penetration having a flame spread rating not more than 25 and a smoke developed rating not more than 50 when tested in accordance with ASTM E 84.  At each end of duct opening provide sealing collars and seal with an interior or exterior and weather resistant non-hardening compound.

#### 3.1.11.3   Ducts Passing Through Equipment Rooms

Provide with sound insulation equal to the sound attenuation value of the wall, floor, or ceiling penetrated.

### 3.1.12   Machinery Foundations and Subbases

Provide cast in place anchor bolts as recommended by the machinery manufacturer.

#### 3.1.12.1   Machinery Subbases

Provide concrete subbases at least 102 mm high for floor mounted equipment. Rest subbases on structural floor and reinforce with steel rods interconnected with floor reinforcing bars by tie bars hooked at both ends. Provide at least 50 mm clearance between subbases and inertia bases, steel bases, and steel saddles with machinery in operation.

#### 3.1.12.2   Common Machinery Foundations

Mount electrical motors on the same foundations as driven machinery. Support piping connections, strainers, valves, and risers on the same foundation as the pumps.

#### 3.1.12.3   Foundation and Subbase Concrete

Cast concrete foundations and subbases of ASTM C 94 20 MPa concrete reinforced with steel bars as indicated or recommended by machinery manufacturer.

3.1.12.4 Anchor Bolts and Grout

Secure machinery to foundations and inertia bases with anchor bolts.  Grout equipment with base plates, the full area under base plates with premixed non-shrinking grout. After grout has set, remove wedges, shims, and jack bolts and fill spaces with grout.

### 3.1.13   Inertia Bases

Install inertia bases in accordance with the recommendations of the machinery manufacturer or inertia base manufacturer, as applicable.

### 3.1.14   Suspended Machinery Platforms

Provide with vibration-isolation hangers.

### 3.1.15   Electrical Connections

Provide flexible conduit or multiple conductor cable connections for machinery with sufficient extra length to permit 50 mm minimum displacement in any direction without damage.

### 3.1.16   Systems Not To Be Vibration Isolated

Do not provide vibration isolation for electrical raceways and conduits or for fire protection, storm, sanitary, and domestic water piping systems, which do not include pumps or other vibrating, rotating, or pulsating equipment including control and pressure reducing valves.

## 3.2   	FIELD QUALITY CONTROL

Provide equipment and apparatus required for performing inspections and tests.  Notify Engineer 14 days prior to machinery sound and vibration testing.  Rebalance, adjust, or replace machinery with noise or vibration levels in excess of those given in the machinery specifications, or machinery manufacturer's data.

### 3.2.1   Field Inspections

Prior to initial operation, inspect the vibration isolators for conformance to drawings, specifications, and manufacturer's data and instructions. Check for vibration and noise transmission through connections, piping, ductwork, foundations, and walls. Check connector alignment before and after filling of system and during operation. Correct misalignment without damage to connector and in accordance with manufacturer's recommendations.

### 3.2.2   Spring Isolator Inspection

After installation of spring isolators or protected spring isolators, and seismic restraint devices, the machinery shall rock freely on its spring isolators within limits of stops or seismic restraint devices.  Eliminate or correct interferences.

### 3.2.3   Tests

Adjust, repair, or replace isolators as required to reduce vibration and noise transmissions to specified levels.

#### 3.2.3.1   Equipment Vibration Tests

Perform vibration tests to determine conformance with vibration isolation schedule specified.

#### 3.2.3.2   Equipment Sound Level Tests

Measure continuous or intermittent steady state noise with a sound level meter set for low response.  Measure impact or impulse noise as dB peak sound pressure level (20 uPa) with an impact noise analyzer.  Measure work distance from person to machinery noise center.  Perform sound level tests to determine conformance with sound level schedule specified.

a.  	Interior Machinery Sound

b. In accordance with ARI 575, measure the sound data for air conditioning & refrigeration machinery, such as fans, boilers, valves, engines, turbines, or transformers. Measure the sound pressure levels around mechanical ainery located in equipment spaces, one meter horizontally from the edge closest to the acoustical center of the machinery at points one meter and 1.68 meter above floor. Take measurements at the center of each side of the machinery. Locate the microphone at least one meter from the observer and measuring instruments. Observer shall not be between the machinery and the measuring instrument.

c. Exterior Machinery Sound

d.  Measure sound data for machinery radiating noise outside the building in such applications as grade installations, area-ways, wall and roof installations for cooling towers, refrigerant condensers, engine driven generator sets, fans, air conditioning machinery, heat pumps, evaporative coolers, exhaust silencers, and air intakes.

End Of Section

SECTION:  4.00

#### LOW PRESSURE DUCTWORK

###### PART 1   GENERAL

This section covers low pressure ductwork that shall be used in all HVAC systems except where modified herein.

1.1   	SUBMITTALS

The following shall be submitted in accordance with relevant sections for Submittal Procedures, in sufficient detail to show full compliance with the specification:

Preconstruction Submittals

Material, Equipment, and Fixture Lists

Shop Drawings

Connection Diagrams Fabrication Drawings Installation Drawings As-Built Drawings

Product Data

Design Analysis and Calculations

Manufacturer's catalog data shall be submitted for the following items:

Galvanized Steel Ductwork Materials Flexible Duct Materials Power Operated Dampers Flexible Connectors Fire Dampers and Wall Collars Gravity Backdraft and Relief Dampers Manual Volume Dampers

Samples

Test Reports

Test reports shall be submitted for low pressure ductwork systems on the following tests in accordance with the paragraph entitled, "Ductwork Leakage Tests" and "Fire Damper Tests," of this section.

1.2   	SCOPE OF WORK

This section covers low pressure ductwork with maximum static pressure below 500 pascal, positive or negative, and maximum duct velocity less than 7.0 m/s.

All ductwork for all operating theaters shall be high pressure duct, and are covered in relevant section for Medium / High Pressure Duct.

All ductwork for dirty exhaust or special extract ducts shall be as per relevant section for Dirty Exhaust and Special Extract Duct.

PART 2   PRODUCTS

2.1   	GALVANIZED STEEL DUCTWORK MATERIALS

Galvanized steel ductwork sheet metal shall be carbon steel, of lock-forming quality, hot-dip galvanized, with regular spangle-type zinc coating, conforming to ASTM A 653/A 653M, Z600.  Duct surfaces to be painted shall be treated by phosphatizing.

Sheet metal gages and reinforcement thickness shall conform to SMACNA, except for minimum standards indicated on drawings.

2.1.1   Duct Hangers

Duct hangers in contact with galvanized duct surfaces shall be galvanized steel painted with inorganic zinc.

2.1.2   Mill-Rolled Reinforcing and Supporting Materials

Mill-rolled structural steel shall conform to ASTM A 36/A 36M and, whenever in contact with sheet metal ducting, shall be galvanized in accordance with ASTM A 123/A 123M.

Equivalent strength, proprietary-design, rolled-steel structural support systems may be submitted for approval in lieu of mill-rolled structural steel.

2.2   	FLEXIBLE DUCT MATERIALS

Flexible duct connectors shall comply with NFPA 90A.

Metal duct shall be bendable through 180 degrees without damage, with an inside bend radius not greater than one-half the diameter of duct.  Metal shall be aluminum zinc-coated ASTM A 123/A 123M.

Wire-reinforced cloth duct shall consist of a chloroprene fibrous-glass cloth bonded to and supported by a corrosion-protected spring steel helix.  Fabric may be a laminate of metallic film and fibrous glass.  Working pressure rating of ducting shall be not less than three times maximum system pressure, and temperature range shall be 29 to plus 79 degrees C.

2.3   	MANUAL VOLUME DAMPERS

Volume damper construction shall conform to SMACNA.

Dampers shall be equipped with an indicating quadrant regulator with a locking feature externally located and easily accessible for adjustment. Where damper rod lengths exceed 760 millimeter, a regulator shall be provided at each end of damper shaft.

All damper shafts shall have two-end bearings.

Splitter damper shall be 0.25 millimeter heavier than duct in which installed.  Hinges shall be full length piano-type.

Damper shaft shall be full length and shall extend beyond damper blade.  A 10 millimeter square shaft shall be used for damper lengths up to 500 millimeter and a 15 millimeter square shaft shall be used for damper lengths 500 millimeter and larger.  Where necessary to prevent damper vibration or slippage, adjustable support rods with locking provisions external to duct shall be provided at damper blade end.

Dampers in ducts having a width perpendicular to the axis of the damper that is greater than 200 millimeter shall be multiblade type having a substantial frame with blades fabricated of 1.6 millimeter metal.  Blades shall not exceed 150 millimeter in width and 1220 millimeter in length and shall be pinned to 15 millimeter diameter shafts.  Dampers greater than 1220 millimeter in width shall be made in two or more sections with intermediate mullions, each section being mechanically interlocked with the adjoining section or sections.  Blades shall have graphite-impregnated nylon bearings and shall be connected so that adjoining blades rotate in opposite directions.

2.4   	GRAVITY BACKDRAFT AND RELIEF DAMPERS

Frame shall be constructed of not less than 40 by 100 millimeter reinforced 1.6 millimeter galvanized carbon steel.  Frames and mullions shall be solidly secured in place and sealed with elastomer calking against air bypass.

Maximum blade width shall be 130 millimeter, and maximum blade length shall be 800 millimeter.  Blade material shall be 1.6 millimeter galvanized steel or 1.99 millimeter 6063 alloy aluminum. Blades shall be provided with mechanically retained seals and 90-degree limit stops.

Dampers used for relief service shall have blades linked together to open not less than 30 degrees on 12 pascal wg differential pressure.

Shaft bearings shall be graphite-impregnated nylon.

Counterbalanced dampers shall be equipped with fixed or adjustable counterbalancing weights.

Gravity backdraft dampers in sizes 460 by 460 millimeter or smaller, when furnished integral with air moving equipment, may be equipment manufacturer's standard construction.

2.5   	FLEXIBLE CONNECTORS FOR SHEET METAL

Connectors shall be UL-listed, .68 kilogram per square meter, fire-retardant, airtight, woven fibrous-glass cloth impregnated with chloroprene.  Clear width, not including clamping section, shall be 76 to 125 millimeter.

2.6   	FIRE DAMPERS AND WALL COLLARS

Fire damper locations shall be in accordance with NFPA 90A.

Fire dampers in ductwork shall be provided at firewall barriers.

Fire dampers shall be constructed and labeled in accordance with UL 555 to provide damper and mounting fire-resistance that equals or exceeds fire-resistance of the construction in which installed.  For link loads in excess of 90 newton, UL-approved quartzoid links shall be provided.

Wall collars shall be constructed in accordance with UL 555.

PART 3 EXECUTIONS

3.1   	INSTALLATION

Sheet metal construction shall be provided in accordance with the SMACNA and NFPA 90A.

Supplementary steel shall be designed and fabricated in accordance with AISC M015L.

Fabrication shall be airtight and shall include necessary reinforcements, bracing, supports, framing, gasketing, sealing, and fastening to provide rigid construction and freedom from vibration, airflow-induced motion, noise, and excessive deflection at specified maximum system air pressure.

Dampers located behind architectural intake or exhaust louvers shall be enclosed by a rigid sheet metal collar and sealed to building construction with elastomers for complete air tightness.

Outside air-intake ducts and plenums shall be sheet metal and shall have soldered watertight joints.

Offsets and transformations shall be provided as required to avoid interference with the building construction, piping, or equipment.

Wherever ducts pass through firewalls or through walls or floors dividing conditioned spaces from unconditioned spaces, a flanged segment shall be provided in that surface during surface construction.

Sheet metal surfaces to be painted or surfaces to which adhesives will be applied shall be clean and free of oil, grease, and deleterious substances.

Where interiors of ducting may be viewed through air diffusion devices, the viewed interior shall be sheet metal and shall be painted flat black.

Duct strength shall be adequate to prevent failure under pressure or vacuum created by fast closure of ductwork devices. Leak tight automatic relief devices shall be provided.

Plenum anchorage provisions, sheet metal joints, and other areas shall be made airtight and watertight by calking mating galvanized steel and concrete surfaces with a two-component elastomer.

3.2   	RECTANGULAR SHEET METAL DUCTS

Angle iron frames shall be welded at corners and ends, whenever possible. Angle iron reinforcements shall be riveted or welded to ducts not more than 150 millimeter on center, with not less than two points of attachment.  Spot welding, where used, shall be 75 millimeter on center.

Standard seam joints shall be sealed with an elastomer compound to comply with SMACNA Seal Class A, B or C as applicable.

Cross breaking shall be limited to 1220 millimeter and shall be provided on all ducts 200 millimeter wide and wider.  Bead reinforcement shall be provided in lieu of cross breaking where panel popping may occur.  Where rigid insulation will be applied, cross breaking is not required.

3.2.1   	Longitudinal Duct Seams: Corner seams shall be Pittsburg lock.

3.2.2   	Joints and Gaskets

Companion angle flanges shall be bolted together with 8 millimeter diameter bolts and nuts spaced 150 millimeter on center.  Flanged joints shall be gasketed with chloroprene full-face gaskets 3 millimeter thick, with Shore A 40 durometer hardness.  Gaskets shall be one piece and vulcanized at joints.

3.2.3   	Flexible Duct Joints

Joints between flexible duct without sheet metal collars and round metal ductwork connections shall be made by trimming the ends, coating the inside of the flexible duct for a distance equal to depth of insertion with elastomer calk, and by securing with sheet metal screws or binding with a strap clamp.

3.2.4 Square Elbows

Single-vane duct turns shall be provided in accordance with SMACNA, and may be used on ducts 300 millimeter wide and narrower.

For all other sizes, double-vane duct turns shall be provided in accordance with SMACNA.

3.2.5   	Radius Elbows

Radius elbows shall conform to SMACNA.  Radius elbows shall have an inside radius equal to the width of the duct.  Where installation conditions preclude use of standard elbows, the inside radius may be reduced to a minimum of 0.25 times duct width and turning vanes shall be installed in accordance with the following schedule.

RADIUS OF TURNING

WIDTH OF ELBOWS        VANES IN PERCENT OF DUCT WIDTH

MILLIMETER       VANE NO. 1          VANE NO. 2    	    VANE NO. 3

Up to 406             	    56        	   	--         	  		--

430 to 120           	    43            		73        	    	--

1245 and over        	    37            		55        	    	83

Where two elbows are placed together in the same plane in ducts 760 millimeter wide and larger, the guide vanes shall be continuous through both elbows rather than spaced in accordance with above schedule.

3.2.6   	Outlets, Inlets, and Duct Branches

Branches, inlets, and outlets shall be installed so that air turbulence will be reduced to a minimum and air volume properly apportioned. Adjustable splitter dampers shall be installed at all supply junctions to permit adjustment of the amount of air entering the branch.  Wherever an air-diffusion device is shown as being installed on the side, top, or bottom of a duct, and whenever a branch takeoff is not of the splitter type, a commercially manufactured air extractor shall be provided to allow adjustment of the air quantity and to provide an even flow of air across the device or duct it services.

Where a duct branch is to handle more than 25 percent of the air handled by the duct main, a complete 90-degree increasing elbow shall be used with an inside radius of 0.75 times branch duct width.  Size of the leading end of the increasing elbow within the main duct shall have the same ratio to the main duct size as the ratio of the related air quantities handled.

Where a duct branch is to handle 25 percent or less of the air handled by the duct main, the branch connection shall have a 45 degree side take-off entry in accordance with SMACNA Fig 2-6.

3.2.7   	Duct Transitions

Where the shape of a duct changes, the angle of the side of the transition piece shall not exceed 15 degrees from the straight run of duct connected thereto.

Where equipment is installed in ductwork, the angle of the side of the transition piece from the straight run of duct connected thereto shall not exceed 15 degrees on the upstream side of the equipment and 22-1/2 degrees on the downstream side of the equipment.

3.2.8   	Branch Connections

Radius tap-ins shall be constructed in accordance with SMACNA.

3.2.9   	Access Openings

Access doors and panels shall be installed in ductwork at controls or at any item requiring periodic inspection, adjustment, maintenance, or cleaning.

Minimum size of access opening shall be 305 by 460millimeter, unless precluded by duct dimensions or otherwise indicated.

Access door construction shall be in accordance with SMACNA, except that sliding doors may be used only for special conditions upon prior approval.  Insulated doors shall be double-panel type.

Access doors that leak shall be made airtight by adding or replacing hinges and latches or by construction of new doors adequately reinforced, hinged, and latched.

3.2.10   Duct Supports

Selection of hanging system shall be at the Contractor's option.  The following support sizes, configurations, and spacings are given to show the minimal type of supporting component required.  Where installed loads are excessive for the specified hanger spacings, hangers, and accessories, heavier-duty components shall be provided or the hanger spacing may be reduced.  After system startup, any duct support device, which, due to length, configuration, or size, vibrates or causes possible failure of a member or damage to ducting shall be replaced or the condition shall be alleviated.

Hanger rods, angles, and straps shall be attached to beam clamps.  Concrete inserts and masonry anchors and fasteners shall be approved for the application.

Ductwork and equipment shall not be hung from piping, or other ducts or equipment.  Maximum span between any two points shall be 3000 millimeter with lesser spans for duct assemblies, interferences, and loads imposed or permitted.

There shall be not less than one set of hangers for each point of support.  Hangers shall be installed on both sides of all duct turns, branch fittings, and transitions.

Hangers shall be sufficiently cross-braced to eliminate vertical and lateral sway.

Single rectangular ducts up to 915 millimeter may be supported by strap hangers attached at not less than three places to not less than three duct surfaces in different planes.

Perforated strap hangers shall not be acceptable.

Rectangular ducting, 915 millimeter and larger, shall be supported by trapeze hangers.  Ducts situated in unconditioned areas and required to have insulation with a vapor-sealed facing shall be supported on trapeze hangers.  Hangers shall be spaced far enough out from the side of the duct to permit the duct insulation to be placed on the duct inside of the trapeze.  Under no circumstances shall duct hangers penetrate the vapor-sealed facing.

Where trapeze hangers are used, the bottom of the duct shall be supported on angles sized as follows:

WIDTH OF DUCT, MILLIMETER     MINIMUM BOTTOM ANGLE SIZE, MILLIMETER

760 and smaller                   		32 by 32 by 3

790 to 1220                 		40 by 40 by 3

1245 to 1830               		40 by 40 by 4.7

1855 to 2440             		        	50 by 50 by 6

2465 and larger        		           	80 by 80 by 6

Where ductwork system contains heavy equipment, excluding air-diffusion devices and single-leaf dampers, such equipment shall be hung independently of the ductwork by means of rods or angles of sizes adequate to support the load.

Duct supports shall be vibration isolated from the structure.

Vibration isolators shall be provided in discharge ducting system for a distance not less than 15 meter beyond the air handling unit.  Deflection of duct and equipment mountings shall be coordinated.

Refer to relevant section for Noise and Vibration Control, for additional requirements.

3.3   	PLENUM CONSTRUCTION

Intake and discharge plenum shall have companion angle joints with the following minimum thickness of materials:

LONGEST          	 SHEET

ANGLES           	METAL                                REINFORCEMENT

SIDE          		USS GAGE     COMPANION ANGLES        INCHES, 610 MM ON

MILLIMETER       ALL SIDES       MILLIMETER             CENTER MAXIMUM

To 1220                 	1.0        	40 by 40 by 3            	40 by 40 by 3

1245 to 2135        	1.3        	50 by 50 by 3           	50 by 50 by 4.7

2160 to 3048        	1.6        	50 by 50 by 3            	50 by 50 by 3

At the floor line and other points where plenums join masonry construction, panels shall be bolted 300 millimeter on center to 50 by 50 by 4.7 millimeter thick hot-dip galvanized steel angle that has been secured to the masonry with masonry anchors and bolts 600 millimeter on center and calked tight to the masonry.

Panels shall be anchored to curbing by not less than 50 by 50 by 4.7 millimeter thick hot-dip galvanized steel angle iron.  Concrete curbing shall include angle iron nosing with welded studs for the anchoring of panels.  Nosing shall be level at curb height within plus or minus 1 millimeter.

Plenum access doors shall be constructed in accordance with SMACNA except that access doors smaller than man-access doors shall have door openings framed with angle iron that is one commercial size smaller than specified panel reinforcement.

Man-access door size shall be per SMACNA and paragraph entitled, "Access Openings," of this section.  Insulated and uninsulated construction shall be per SMACNA.  Door openings shall be framed with channel iron.  Doors shall be framed with angle iron.  Channel iron and angle iron shall be approximately the same size as specified panel reinforcement.  Exterior door skin shall be 1.6 millimeter.  Latches shall be fabricated steel, hinges shall be at least 100 millimeter long, and bolting shall be at least 10 millimeter diameter.

Angle iron and channel iron shall have welded and ground miter corners.

3.4   	MANUAL VOLUME DAMPERS

Balancing dampers of the splitter, butterfly, or multi louver type, shall be provided to balance each respective main and branch duct.

Dampers regulated through ceilings shall have regulator concealed in box mounted in the ceiling, with a cover finish aesthetically compatible with ceiling surface.  Where ceiling is of removable construction, regulators shall be above ceiling, and location shall be marked on ceiling in a manner acceptable to the Contracting Officer.

3.5   	FLEXIBLE CONNECTORS FOR SHEET METAL

Air handling equipment, ducts crossing building expansion joints, and fan inlets and outlets shall be connected to upstream and downstream components by treated woven-cloth connectors.

Connectors shall be installed only after system fans are operative, and vibration isolation mountings have been adjusted.  When system fans are operating, connectors shall be free of wrinkle caused by misalignment or fan reaction.  Width of surface shall be curvilinear.

3.6   	INSULATION PROTECTION ANGLES

Galvanized 1.0 millimeter sheet steel, formed into an angle with a 50 millimeter exposed long leg with a 10 millimeter stiffening break at outer edge, and with a variable concealed leg, depending upon insulation thickness shall be provided.

Angles shall be installed over insulation edges terminating by butting against a wall, floor foundation, frame, and similar construction.  Angles shall be fastened in place with blind rivets through the protection angle, insulation, and sheet metal duct or plenum.  Angles shall be installed after final insulation covering has been applied.

3.7   	DUCT PROBE ACCESS

Holes shall be provided with neat patches, threaded plugs, or threaded or twist-on caps where indicated, and where necessary, for air-balancing pitot tube access.  Extended-neck fittings shall be provided where probe access area is insulated.

3.8   	OPENINGS IN ROOFS AND WALLS

Building openings are fixed and equipment shall be provided to suit.  Contractor may propose to alter these openings upon prior approval, and at his expense.

3.9   	DUCTWORK CLEANING PROVISIONS

Open ducting shall be protected from construction dust and debris in a manner approved by the Engineer.  Dirty assembled ducting shall be cleaned by subjecting main and branch interior surfaces to air streams moving at velocities two times the specified working velocities, at static pressures within maximum ratings.  Ducting shall be cleaned by a method approved by the Contracting Officer.  Compressed air used for cleaning ducting shall be water- and oil-free.  Prior to acceptance of the work, dust and debris shall be removed from exterior surfaces.

3.10   	FIRE DAMPER TESTS

Operation tests shall be performed on each fire damper in the presence of the Engineer by enervating fusible link with localized heat.  New links shall be provided and installed after successful testing.

3.11   	DUCTWORK LEAKAGE TESTS

Leak test the HVAC air duct sections of each system as selected by the Engineer.  Use the duct class, seal class, leakage class and the leak test pressure data indicated on the drawings, to comply with the procedures specified in SMACNA Leakage Test Mnl.  Testing shall be in accordance with the procedures specified in SMACNA Leakage Test Mnl, except as supplemented and modified by this section.

3.12   	OPERATION AND MAINTENANCE

Operation and Maintenance Manuals shall be consistent with manufacturer's standard brochures, schematics, printed instructions, general operating procedures and safety precautions.

End Of Section

SECTION:  5.00

###### DIRTY EXHAUST AND SPECIAL EXTRACT/INTAKE SYSTEMS

PART 1   GENERAL

This section covers all dirty and special extract systems including fans, filters, ductwork and workmanship. Round steel ducts shall be covered in Medium/High Pressure Duct Section as specified herein.

1.1   	GENERAL REQUIREMENTS

1.1.1   	SMACNA Duct Construction Manuals

The recommendations in the Sheet Metal and Air Conditioning Contractors' National Association (SMACNA) duct construction manuals shall be considered mandatory requirements. Substitute the word "shall" for "should" in these manuals.

1.1.2   	Dirty Extract Systems

Dirty extract duct work shall be single wall galvanized steel duct as per relevant specifications for Low pressure duct. Dirty extract fans and other components shall be as specified in this section.

1.1.3   	Special Extract Systems

Special extract duct work shall be PVC as specified in this section.

Special extract duct work serving kitchen Hoods shall be Corrosion Resistant (Stainless) Steel to ASTM A 167, Type 304L or Type 316L with mill finish, as specified in this section.

Special extract/intake fans and accessories shall be as specified in this section.

1.1.4   	Dirty Exhaust and Special Extract Systems

Submit drawings including fan installation drawings; duct systems, supports and anchor location and load imposed.

1.2   	SUBMITTALS

Submit the following in accordance with relevant section for Submittal Procedures.

Shop Drawings

Dirty exhaust and special extract systems

Product Data

Fans

Dampers

Flexible connectors

Flexible duct

Gaskets

Sealants

Access ports

Damper regulators

Supports and hangers

Vibration isolators

THERMOPLASTIC ductwork

Test Reports

Fan tests

Sound level tests

Operation and Maintenance Data

Ventilation and exhaust systems

Closeout Submittals

1.3   	POSTED OPERATING INSTRUCTIONS

Provide for ventilation and exhaust system.  In addition, permanently mark, drill, and pin as an integral part of device, final adjustment and settings pursuant to testing, adjusting, and balancing.

PART 2   PRODUCTS

2.1   	FANS, GENERAL REQUIREMENTS FOR

2.1.1   General Performance, Component, and Other Requirements

Fans shall have certified performance ratings as evidenced by conformance to the requirements of AMCA 211, and shall be listed in AMCA 261, or shall be currently eligible for such listing. Fans shall generally be in accordance with AMCA 99 unless superseded by other requirements stated elsewhere herein.  Determine performance data for fans in accordance with AMCA 210. Select fans to minimize the exposure of personnel working in or occupying the immediate installation area. The total sound power level of the fan tests shall not exceed 90 dBA when tested per AMCA 300 and rated per AMCA 301, or it shall be provided with an appropriate attenuation device or devices. Scheduled fan performance is the performance required under specified or indicated installation conditions with specified or indicated accessories. The net installed air performance of the fan, with accessories/appurtenances in place, shall be sufficient to meet the scheduled performance within the limits of the fan rating certification tolerance. Affix the manufacturer's product identification nameplate to each unit. Apply additional requirements for specific service or generic type or class of fan. If non uniform air flow conditions are likely to be encountered, contact the fan manufacturer to ensure that the fan is rated for the additional fan inlet and outlet effect. Install fans to minimize fan system effect in accordance with AMCA 201.  Fans shall be listed in the Directory of Products licensed to use AMCA seal.

2.1.2   	Bearings and Lubrication

Precision anti-friction or sleeve type with provisions for self-alignment and for radial and thrust loads imposed by the service.  Provide water-cooled bearings where required for the service or recommended by the manufacturer.

2.1.2.1   Anti-friction Bearings

Constructed of steel alloys with a certified L-10 minimum rated life of 80,000 hours under load conditions imposed by the service. Rated and selected in accordance with ABMA 9 and ABMA 11. Provide with dust-tight seals suitable for environment and lubricant pressures encountered; cast ferrous metal housing, bolted-split pillow block type where located within fan casings; grease lubricated with provisions to prevent overheating due to excess lubricant; surface ball check type grease supply fittings. Provide manual or automatic grease pressure relief fittings visible from normal maintenance locations. Include lubrication extension tubes where necessary to facilitate safe maintenance during operation and fill tubes with lubricant prior to equipment operation.  Prelubricated, sealed, anti-friction bearings, which conform to above specified materials and L-10 life requirements, may be provided for fans requiring less than 0.37 kW.

2.1.2.2 Sleeve Bearings

Premounted, self-aligning, continuous oil supply, single or double ring lubricated, insert type, with suitable provisions for shaft expansion and such thrust as may be imposed by service loads. Provide water cooling for shaft surface speed exceeding 6.1 meters per second. Provide each sleeve bearing with approximately 473 mL capacity constant level oiler and oil level gage. Include on sleeve bearing submittal data: Bearing manufacturing source, type, lubricant, clearances, "L/D" ratio, antifriction metal, belt angle, shaft speed, shaft critical speed, Brinell hardness at journal, and shaft surface finish at journal in micro-inches.

2.1.3   	Motors and Motor Starters

Conform to NEMA MG 1 and NEMA ICS 1 and NEMA ICS 2. Motors shall not exceed 14500 rpm, unless otherwise indicated, and shall be totally enclosed fan cooled type. Fan motors where may be exposed to combustable fumes shall be explosion proof type. Up to 3.5 kW motors, provide magnetic-across-the-line motor starter. 3.5 kW and above, provide wye-delta type motor starters. All motor starters shall comply with moisture and dust tight NEMA 12 enclosure in accordance with NEMA ICS 6. Provide single-phase motors with inherent thermal overload protection with manual reset. Provide three-phase motors with thermal overload protection in the control panel. Provide permanently lubricated or grease-lubricated ball or roller bearings; auxiliary lubrication and relief fittings on outside of fan casing; arrange grease lines to minimize pressure on bearing seals. Motor power shall not be less than brake power required with blades set at maximum pitch angle at any air delivery from the indicated amount down to 50 percent thereof.

2.1.4   Guards and Screens

Construct guards and screens to provide, as applicable: required strength and clearance with minimal reduction in free area at fan inlets and discharges; cooling; access panels for tachometer readings; ease of sectional disassembly for maintenance and inspection functions where guard total weight exceeds 22.70 kg; weather protection where components are weather exposed. Installed guards & screens shall not negate noise control and vibration isolation provisions. For burn protection, insulate surfaces when service temperatures exceed 60 degrees C as part of work under relevant section for "Mechanical Insulation."

2.1.5   	Power Transmission Components

2.1.5.1   Fan Drives

Direct or V-belt type, single or twin type, as indicated. V-belt drives shall conform to ANSI IP-20 and ANSI IP-22. Drives shall be applied in accordance with the manufacturer's published recommendations, unless specified otherwise. Base power rating of a V-belt drive on maximum pitch diameter of sheaves. Provide classical belt section adjustable sheave type, with a minimum service factor of 1.5 for drives with motors rated up to and including 22 kW. Provide classical section or narrow section, fixed sheave or adjustable sheave type with a minimum 1.5 service factor for drives with motors rated over 22 kW. Provide at least two belts for drives with motors rated one hp and above.

2.1.5.2   Sheaves

Statically and dynamically balanced, machined cast ferrous metal or machined carbon steel, bushing type, secured by key and keyway. Pitch diameter or fixed sheaves and adjustable sheaves, when adjusted to specified limits, shall not be less than that recommended by NEMA MG 1.  Select adjustable sheaves that provide the required operating speed with the sheave set at midpoint of its adjustment range. The adjustment range for various size and type belts shall be:  16 percent, minimum for Classical section belts; 12 percent, minimum for Narrow section belts. Belt deflection in adjustable sheave drives shall not exceed 1 1/2 degrees. Provide companion sheaves for adjustable sheave drives with wide groove spacing to match driving sheaves, except that standard fixed pitch spacing may be used for all two-through-four groove drives whose center-to-center dimensions exceed the following: "A" and "B" Section 406 mm; "C" Section 635 mm; "D" Section 914 mm. Furnish endless, static dissipating, oil-resistant, synthetic cloth or filament reinforced elastomer construction belts.

2.1.6   	Special Extract in Hazardous Areas

2.1.6.1   Spark-Resistant

Construct specified or indicated units in accordance with AMCA 99-0401-66; Type A. Provide Type C construction and electrical grounding of fan parts and grounding to building structure where fume or vapor handling systems conforming to NFPA 91 are specified.

2.1.6.2   Explosion Proof

Construct fans to AMCA 99-0401-66, Type C spark-resistant requirements where explosion-proof electrical components are specified or indicated to conform to NFPA 70, requirements.

2.1.7   Protective Coating for Fans

Factory applied protective coating shall be required for all fume hood fans, ETO extract fans, and any fand where exposed to fume or vapor streams. Prepare and coat fans as follows: Replace bolts required to provide access or adjustment and normally threaded into the coated surface with studs or bolts having heads continuously welded inside. Omit sharp edges, self-tapping screws, and permanent threads protruding into the coated surface. Eliminate hairline cracks and sharp inside corners by continuous welding, brazing, or filling with high melting point solder. Seal impeller hub to the shaft. Construct housing split to use external through bolts. Flange inlet and outlet and consider as fan interior.  Peen or grind welds smooth, and grind outside corners to approximately 1.60 mm radius. Sandblast metal surfaces to white metal in accordance with SSPC SP 5Coat interior surfaces of housing in contact with airstream, including inlet, impeller and shaft, flange faces, shaft seal, and bearing and motor pedestal.  Do not coat bearings, coupling, motor, drive, or other auxiliaries. Finish fan in accordance with the manufacturer's standard practice. Statically and dynamically balance the fan in two planes after coating and finishing, and where material has been removed, refinish and rebalance the fan as specified herein.

2.2   	CENTRIFUGAL FANS

2.2.1   General Requirements for Centrifugal Fans

Provide fan of backward inclined type blades with manual inlet vanes. Arrange fans for indicated service, and construct for the applicable AMCA 99 Class pressure ratings as indicated for system design pressure and temperature. Fan shaft shall be solid steel, ground and finished as required for the service, with first critical speed a minimum 25 percent higher than cataloged fan speed.  Select fan for maximum efficiency, minimum noise, and stability during all modes of system operation. Vibration isolation mountings shall be spring type and limit vibration transmissibility to a maximum 5 percent of the unbalanced force at lowest equipment speed, unless otherwise specified or indicated. Arrangement and drives shall be as indicated.

2.2.2   In-line/Cabinet Centrifugal Fans

Welded steel casings, centrifugal backward inclined blades, stationary discharge conversion vanes, internal and external belt guards and adjustable motor mounts. Inlet and outlet connections for fan casings to duct work and equipment casings, may be of the slip fit or flanged type. Provide guards for discharges.  Rate fans with guards in place. Air shall enter and leave the fan axially. Inlet shall be streamlined and conversion vanes shall eliminate turbulence and provide smooth discharge air flow. Enclose fan bearings and drive shafts, and isolate from the air stream. Fan bearings shall be mechanically sealed against dust and dirt and shall be self-aligning, pillow block ball or roller type. Motor and drive shall be provided by fan manufacturer.

2.2.3   Roof Top Fans

AMCA 210 with AMCA seal, centrifugal belt or direct driven fans in spun aluminum housings high-impact plastic with glass fiber reinforcement. Equip motors with unfused safety disconnect switches mounted under fan housings and resilient mounts. Mount motors out of air stream. Provide factory-fabricated roof curbs with continuous curb gaskets and aluminum bird screen. Provide gravity actuated, aluminum multiple blade construction backdraft damper and cast iron or steel sheaves, dynamically balanced & bored to fit shafts and keyed.

2.2.4   Vibration Isolation

For the entire fan, motor, and drive assembly, provide 50 mm nominal deflection spring vibration isolators, internally mounted at the factory together with fan discharge flexible connection and thrust restraint springs.

2.2.5   Exhaust Terminal Filters

Provide terminal filters set on all dirty extract fans, and on special extract fans as indicated. The terminal filters set shall be composed of synthetic bag filter of 600 mm depth, synthetic pleated pre-filter all enclosed in filter housing with exhaust terminal unit, except where otherwise indicated.

The above components material, installation and inspection shall be as per relevant section for Air Handling and Air Conditioning Equipment.

2.3   	AXIAL FANS

2.3.1 Axial Wall/Box Fans:

Direct drive wall mounted or Box fans shall construct of one-piece bell mouth inlet and mounting plate manufactured from pressed galvanized steel. This mounting plate assembly shall be protected by a tough beige polyester paint finish the fan motor and impeller shall be supported within the mounting plate by a strong steel support frame. The fan shall include a steel finger proof guard as standard mounted to the inlet side of the fan. Both the motor support and finger guard are protected by a primer and tough being color polyester paint finish. The fans shall have impeller manufactured by galvanized steel sheet and finished with a black epoxy- polyester paint for capacities under 1000cfm (500 L/s). The impellers are factory matched and balanced onto the corresponding motors. The fan motor shall be single phase shaded pole asynchronous induction motors with squirrel cage rotor in die cast aluminum for capacities under 1000cfm (500L/s). The fans shall be supplied with a flexible cable for connection to the electrical supply. For the high corrosion resistance application or where capacities exceeds 1000cfm (500 L/s). The fan impellers shall be of one die cat aluminum, motor protection rate not less than IP 55, Class F insulation (-40 C to +70 C working temperature), scaled for life ball bearing, if required the fan must be suitable for usage in environments up to 95% RH, manufactured with special motor breath holes to allow condensation to escape while eliminating water ingress when the fan is used in very humid environments and at low temperature, the impellers is fitted with special drainage holes to prevent the ingress and collection of water when used in exterior mounted installations. The fan assembly is protected by tough black polyester paint finish. This particular coating has been evaluated as being suitable for outdoor equipment usage, by underwriters laboratories, inc (USA). The fans shall be fulfill to AMCA, BS, or ASHRAE Standards.

3.2 Window/ Wall Plastic Axial Fans:

AUTOMATIC SHUTTER FANS. The fans shall be manufactured from injection molded plastic within the following features, single phase motor 220-240v, 50Hz with thermal protection, class II insulation,tow speed operation, automatic thermally actuated shutter, neon light mode of operation indication complete with wire guard, when the fans installed the contractor should take care for the various wall thickness.

2.4   	FIRE DAMPERS

Provide single curtain type with interlocking blades with frame and operating mechanism housed out-of-stream, constructed and rated in accordance with AMCA 500. Furnish dampers for indicated stream flow, to equal or exceed fire resistance rating of 1 1/2 hours. Fire damper shall be rattle-free and shall cause a minimum 5 percent increase in stream velocity or system static pressure. Provide building penetration collars in accordance with AMCA 500 and NFPA 91. Provide one spare fusible link for testing of each fire damper operation and one spare fusible link for each 10 fire dampers, but not less than two.

2.5   	THERMOPLASTIC DUCTWORK

2.5.1   Ductwork

Construct ductwork, fittings, hoods, and accessories in accordance with SMACNA and NFPA 91.

2.5.2   Product Requirements

Provide duct system from a manufacturer recognized in the field of fabrication of PVC material. Fabricating personnel shall be certified by the manufacturer as qualified to perform the work in accordance with the specified requirements.

2.5.3   Basic Ductwork Materials

Fabricate ducts, hoods, accessories and components in sheet form from materials conforming to ASTM D 1927, Type I, Grade 2.  Utilize extrusions of the same compounds as specified for duct.  Solvent cement shall conform to ASTM D 2564. Construct metal components, when permitted to be located interior to the duct, of Type 316 or 316L [corrosion resistant steel].

2.5.4   Fasteners

Where penetration of duct surfaces is approved or specified, provide Type 316 corrosion resistant steel fastener assemblies encapsulated with polyster on duct interior, unless total disassembly is intended. Provide flange fastener bolts and nuts of hex type only, cadmium plated, unless exposed to corrosive fumes; in which case provide Type 316 stainless steel. Equip bolted assemblies with two oversized washers, except where assembled with metallic reinforcement contact. Plastic bolting is prohibited.

2.5.5   Joint Gaskets

Provide 3 mm thick acid resistant chloroprene.

2.5.6   Fabrication

Construct water washable, watertight, self-draining, and airtight ductwork as specified or indicated. Provide required reinforcements, bracing, supports, framing, gasketing, sealing, resilient mounting, drainage provisions, & fastening to guarantee rigid construction and freedom from vibration, airflow induced motion and noise, and excessive deflection at specified maximum system pressure and velocity.

2.5.6.1   Flanges

Provide flanges at all branches on maximum 6 meters centers in ducting sized 400 mm and under, on maximum 2.40 meters centers in duct sized over 400 mm, where required for ease of access to equipment, at hoods, enclosure connections & where indicated. Furnish one piece, heat, adhesive, or solvent vulcanized or bonded full face gaskets at flange joints.

2.5.6.2   Access Plates

Provide access plates upstream and downstream of equipment in ducts at locations to facilitate duct cleaning, and where indicated. Locate access openings a minimum of 50mm above bottom of duct & externally frame with welded and ground miter joint steel, which is isolated from duct interior.  Construct access plate with PVC on interior side, backed with steel on exterior side. Provide stainless steel access plate fasteners.  For ductwork cleaning access, provide 200mm diameter gasketed access plates on maximum 3 meters on centers, except where access is available through an air terminal device or other required access.

  - CORROSION RESISTANT (STAINLESS) STEEL DUCTWORK:

Sheet material shall be ASTM A 167, Type 304L or Type 316L with mill finish.

Construct ductwork to handle corrosive & flammable fumes and vapors containing ETO. Spiral welded duct is prohibited. Provided ductwork in accordance with best practice recommendations and requirements of SMACNA for Class IV duct.

Provide indicated sizes, lengths and configuration without deviation, unless otherwise approved. Spiral welded duct is prohibited. Install ductwork to be water washable, watertight, self-draining, & airtight Provide necessary reinforcements, bracing supports, framing, gasketing, & drainage provisions, & fastening to guarantee rigid construction & freedom from vibration, airflow induced motion, and excessive deflection. Rigid construction is required to prevent damage to or failure of protective coating during construction, transport, erection, and on-off system operation. Only companion angle flanged joints shall be permitted.

2.6   	STACKHEADS

Provide SMACNA Industry Practice no loss type stack heads for vertical discharge to the atmosphere unless indicated otherwise.  Weather caps are prohibited.  Provide bracing or guy wires for wind loads on stacks as indicated.  Discharge stacks should be vertical and terminate at a point where height or velocity prevents reentry of exhaust air.

PART 3 EXECUTIONS

3.1   	INSTALLATION

3.1.1   Installation Requirements

Install in accordance to NFPA91, & SMACNA RIDCSTD, & SMACNA RIDCS. Provide mounting & supports for equipment, ductwork, & accessories, including structural supports, hangers, vibration isolators, stands, clamps and brackets, access doors, blast gates, & dampers.  Install accessories in accordance with the manufacturer's instructions. Construct positive pressure duct inside buildings airtight.

3.1.2   Special Requirements for Installation of Thermoplastic Ductwork

Requirements for installation of thermoplastic ductwork for nonflammable corrosive fume and vapor exhaust:

3.1.2.1   Slope

Slope horizontal ducts 25 mm in 12 meters in the direction of airflow or 25 in 3 meters in opposite to the direction of airflow.  Where necessary, slope duct to common drainage point.

3.1.2.2   Drains

Provide drains at all low points, at internal to duct drainage restrictions, at base of risers, and where indicated.  Provide drain connections of 25 mm IPS couplings with polytetrafluoroethylene paste lubricated plug where drainage piping is not indicated, and where piping is indicated, provide PVC Type DWV piping conforming to ASTM D 2665 to points indicated.  Provide trap of 25 mm greater depth than the positive or negative pressure in the duct but not less than 50 mm.

3.1.2.3   Duct Supports

Isolate duct support contact surfaces from supporting steel by 6 mm thick closed-cell foamed cellular elastomer insulation material of a width greater than support.  Provide duct support system to include additional weight due to collection of condensate and washing water in non drainable, deflected surface and other areas.

3.1.3   Building Penetrations

3.1.3.1   General Penetration Requirements

Provide properly sized, fabricated, located, and trade coordinated sleeves and prepared openings, for duct mains, branches, and other item penetrations, during the construction of the surface to be penetrated. Provide sleeves for round duct 380 mm and smaller and prepared openings for round duct larger than 380 mm and square or rectangular duct.  Fabricate sleeves, except as otherwise specified or indicated, from 20 gage, 1.00 mm thick mill galvanized sheet metal.

3.1.3.2   Framed Opening

Provide framed openings in accordance with approved shop drawings. Refer to paragraph entitled "Fire Dampers," in this section, for related work.

3.1.3.3   Clearances

Provide a minimum 25mm clearance between penetrating & penetrated surfaces. Fill clearance space with bulk fibrous glass or mineral wood and seal and close.

3.1.3.4   Tightness

Penetration shall be weather tight, fireproof where fire rated surfaces are penetrated, vapor tight to prevent vapor transmission to conditioned spaces, sound tight to prevent sound transmission to or between normally occupied or finished spaces.

3.1.3.5   Sealants

Provide sealant of elastomeric type or foamed silicone type.  Apply to oil free surfaces to a minimum 10 mm depth.

3.1.3.6   Closure Collars

Provide a minimum 100mm wide, unless otherwise indicated, for exposed ducts & items on each side of penetrated surface, except where equipment is installed. Install collar tight against the surface and fit snugly around penetrating item without contact. Grind sharp edges smooth to prevent damage to penetrating surface. Fabricate collars for round ducts 380mm in diameter or less from 20 gage, 1.00mm nominal thickness, mill galvanized steel. Attach collars a minimum of 4 fasteners to where the opening is 300mm in diameter or less, and a minimum of 8 fasteners where the opening is 500mm in diameter or less. Fabricate collars for square & rectangular ducts with a maximum side of 380mm or less from 20 gage, 1.00mm nominal thickness, mill galvanized steel. Fabricate collars for round, square, & rectangular ducts with minimum dimension over 380mm from 18 gage, 1.40mm in nominal thickness, mill galvanized steel. Install collars with fasteners a maximum of 150mm on center. Where penetrating items are irregularly shaped & where approved, smoothly finished, fire-retardant, foamed silicone elastomer may be utilized without closure collar.

3.1.4   Installation of Fire Dampers

Install fire dampers at locations indicated. Provide units & connecting ductwork in accordance with applicable provisions of NFPA 91. Install retaining angles, sleeves, break-away connections, & duct access doors at each damper, as required. Minimum thickness of sleeves shall be 14 gage. Duct access doors shall be hinged. Prior to acceptance, simulate conditions to cause each unit to function automatically. Apply safe, non flame, heat source to fusible links and replace test activated fusible links.

3.1.5   Installation of Flexible Connectors

Flexibly connect duct connected & vibration isolated fans, ducts crossing building expansion joints & specified or indicated components. When fans are started, stopped, or operating, flexible connector surfaces shall be curvilinear, free of stress induced by misalignment or fan reaction forces, & shall not transmit vibration. Leakage shall not be perceptible to the hand when placed within 150 mm of the flexible connector surface or joint. Provide a minimum of 150mm and a maximum of 610mm active length with a minimum of 25mm of slack, secured at each end by folding in to 24 gage sheet metal or by metal collar frames.

3.1.6   Installation of Supports

3.1.6.1   Selection

Select duct and equipment support system taking into account the best practice recommendations and requirements of SMACNA and NFPA 91.

3.1.7   Ductwork Cleaning

Protect duct openings from construction debris using temporary caps, flanges, or other approved means. Clean dirty duct interior with high velocity water & oil-free air streams or by vacuum cleaning as required by project conditions. After construction is complete but accessible & prior to acceptance, remove all construction debris from exterior surfaces. Do not close duct inspection ports until inspected by the Engineer.

3.1.8   Factory Painting and Finishing

3.1.8.1   Factory Work

Factory finish interior ferrous metal & other specified metallic equipment & component surfaces with manufacturer's standard surface preparation, primer, & finish coating. Factory finish exterior to building space ferrous metal surfaces & other exterior to building & interior to building metallic or non metallic surfaces with specified protective coating system in accordance with the paragraph entitled "Protective Coating Material," in this section & otherwise with manufacturer's standard surface prepara-tion, primer & finish which meet the requirements of paragraph entitled "Corrosion Prevention."

3.2   	TESTING, ADJUSTING, AND BALANCING

3.2.1   Ductwork Structural Integrity and Leakage Testing

Inspect and test systems pressure rated higher than 398 Pa gage for structural integrity and leakage as systems or sections during construction but after erection, as work progresses, in system or section lengths not exceeding 30 meters. Test for structural integrity at 25 percent in excess of system fan positive or negative total pressure. Test for leakage at 25 percent in excess of system fan positive or negative total pressure. Leakage test procedure and apparatus shall be in accordance with SMACNA Leakage Test Mnl. Total leakage, prorated to length of duct under test, shall not exceed one percent of system capacity.

3.2.2   Power Transmission Components Adjustment

Test and adjust V-belts and sheaves for proper alignment and tension preliminary to operation and after 72 hours of operation at final speed, in the presence of the Engineer. Belts on drive side shall be uniformly loaded, not bouncing. Align direct-drive couplings to less than half of manufacturer's allowable range of misalignment.

3.2.3   Preliminary Tests

Conduct an operational test on the entire exhaust duct systems, components, and equipment for a period of not less than 6 hours after power transmission components are adjusted. Replace filters, if any, after preliminary tests and prior to conducting final acceptance tests.

3.2.4   Testing, Adjusting, and Balancing Work

Perform work in accordance with the applicable & recommended procedures of: ACGIH-2092. Provide apparatus, certified, calibrated, instrumentation including that to measure sound levels, motor current, and power factor. Unless approved otherwise, instruments shall be limited to manometers and approved aneroid type gages (such as a Magnehelic). Velometers may be used for low velocity measurements if approved by the Engineer.

3.2.5   	Systems Volume Acceptance Criteria

Systems final volume shall be within the following limits:

Fan:  Plus 10 percent of design volume at design temperature

Hood or Equipment: Plus or minus 5 percent of design volume at design temperature

Note: Tolerances shall be taken on clean or dirty conditions as indicated on the drawings.

End Of Section

SECTION:  6.00

AIR CONDITIONING (SUPPLY & RETURN) DUCTS

- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

      - SUMMARY

        - Section Includes:

          - Single-wall rectangular ducts and fittings.

          - Sheet metal materials.

          - Duct liner.

          - Sealants and gaskets.

          - Hangers and supports.

          - Seismic-restraint devices.

        - Related Sections:

          - Division 15 Section "Nonmetal Ducts" for fibrous-glass ducts, thermoset fiber-reinforced plastic ducts, thermoplastic ducts, PVC ducts, and concrete ducts.

          - Division 15 Section "HVAC Casings" for factory- and field-fabricated casings for mechanical equipment.

          - Division 15 Section "Duct Accessories" for dampers, sound-control devices, duct-mounting access doors and panels, turning vanes, and flexible ducts.

          - Division 15 Section "Testing, Adjusting, and Balancing" for testing, adjusting, and balancing requirements for metal ducts.

      - PERFORMANCE REQUIREMENTS

        - Delegated Duct Design:  Duct construction, including sheet metal thicknesses, seam and joint construction, reinforcements, and hangers and supports, shall comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible".

        - Structural Performance:  Duct hangers and supports and seismic restraints shall withstand the effects of gravity and seismic loads and stresses within limits and under conditions described in SMACNA's "HVAC Duct Construction Standards - Metal and Flexible".

      - SUBMITTALS

        - Product Data:  For each type of the following products:

          - Liners and adhesives.

          - Sealants and gaskets.

          - Seismic-restraint devices.

        - Shop Drawings:

          - Fabrication, assembly, and installation, including plans, elevations, sections, components, and attachments to other work.

          - Factory- and shop-fabricated ducts and fittings.

          - Duct layout indicating sizes, configuration, liner material, and static-pressure classes.

          - Elevation of top of ducts.

          - Dimensions of main duct runs from building grid lines.

          - Fittings.

          - Reinforcement and spacing.

          - Seam and joint construction.

          - Penetrations through fire-rated and other partitions.

          - Equipment installation based on equipment being used on Project.

          - Locations for duct accessories, including dampers, turning vanes, and access doors and panels.

          - Hangers and supports, including methods for duct and building attachment , seismic restraints, and vibration isolation.

        - Welding certificates.

        - Field quality-control reports.

- PRODUCTS

      - SINGLE-WALL RECTANGULAR DUCTS AND FITTINGS

        - General Fabrication Requirements:  Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" based on indicated static-pressure class unless otherwise indicated.

      - SHEET METAL MATERIALS

        - General Material Requirements:  Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" for acceptable materials, material thicknesses, and duct construction methods unless otherwise indicated.  Sheet metal materials shall be free of pitting, seam marks, roller marks, stains, discolorations, and other imperfections.

        - Galvanized Sheet Steel:  Comply with ASTM A 653/A 653M.

          - Galvanized Coating Designation:  G90 (Z275).

          - Finishes for Surfaces Exposed to View:  Mill phosphatized.

        - PVC-Coated, Galvanized Sheet Steel:  Comply with ASTM A 653/A 653M.

          - Galvanized Coating Designation:  G90 (Z275).

          - Minimum Thickness for Factory-Applied PVC Coating:  4 mils (0.10 mm) thick on sheet metal surface of ducts and fittings exposed to corrosive conditions, and minimum 1 mil (0.025 mm) thick on opposite surface.

          - Coating Materials:  Acceptable to authorities having jurisdiction for use on ducts listed and labeled by an NRTL for compliance with UL 181, Class 1.

        - Carbon-Steel Sheets:  Comply with ASTM A 1008/A 1008M, with oiled, matte finish for exposed ducts.

        - Stainless-Steel Sheets:  Comply with ASTM A 480/A 480M, Type 304 or 316, as indicated in the "Duct Schedule" Article; cold rolled, annealed, sheet.  Exposed surface finish shall be No. 2B, No. 2D, No. 3, or No. 4 as indicated in the "Duct Schedule" Article.

        - Aluminum Sheets:  Comply with ASTM B 209 (ASTM B 209M) Alloy 3003, H14 temper; with mill finish for concealed ducts, and standard, one-side bright finish for duct surfaces exposed to view.

      - DUCT LINER

        - Fibrous-Glass Duct Liner:  Comply with ASTM C 1071, NFPA 90A, or NFPA 90B; and with NAIMA AH124, "Fibrous Glass Duct Liner Standard."

- -	Type II, Rigid:  (0.033 W/m x K) at 75 deg F (24 deg C) mean temperature.

        - Natural-Fiber Duct Liner:  85 percent cotton, 10 percent borate, and 5 percent polybinding fibers, treated with a microbial growth inhibitor and complying with NFPA 90A or NFPA 90B.

        - Insulation Pins and Washers:

          - Cupped-Head, Capacitor-Discharge-Weld Pins:  Copper- or zinc-coated steel pin, fully annealed for capacitor-discharge welding.

          - Insulation-Retaining Washers:  Self-locking washers formed from 0.016-inch- (0.41-mm) thick galvanized steel; with beveled edge sized as required to hold insulation securely in place but not less than 1-1/2 inches (38 mm) in diameter.

      - SEALANT AND GASKETS

        - General Sealant and Gasket Requirements:  Surface-burning characteristics for sealants and gaskets shall be a maximum flame-spread index of 25 and a maximum smoke-developed index of 50 when tested according to UL 723; certified by an NRTL.

        - Two-Part Tape Sealing System:

          - Tape:  Woven cotton fiber impregnated with mineral gypsum and modified acrylic/silicone activator to react exothermically with tape to form hard, durable, airtight seal.

          - Tape Width:  3 inches (76 mm).

          - Sealant:  Modified styrene acrylic.

          - Water resistant.

          - Mold and mildew resistant.

          - Maximum Static-Pressure Class:  10-inch wg (2500 Pa), positive and negative.

          - Service:  Indoor and outdoor.

          - Service Temperature:  Minus 40 to plus 200 deg F (Minus 40 to plus 93 deg C).

          - Substrate:  Compatible with galvanized sheet steel (both PVC coated and bare), stainless steel, or aluminum.

        - Water-Based Joint and Seam Sealant:

          - Application Method:  Brush on.

          - Solids Content:  Minimum 65 percent.

          - Shore A Hardness:  Minimum 20.

          - Water resistant.

          - Mold and mildew resistant.

          - VOC:  Maximum 75 g/L (less water).

          - Maximum Static-Pressure Class:  10-inch wg (2500 Pa), positive and negative.

          - Service:  Indoor or outdoor.

          - Substrate:  Compatible with galvanized sheet steel (both PVC coated and bare), stainless steel, or aluminum sheets.

        - Solvent-Based Joint and Seam Sealant:

          - Application Method:  Brush on.

          - Base:  Synthetic rubber resin.

          - Solvent:  Toluene and heptane.

          - Solids Content:  Minimum 60 percent.

          - Shore A Hardness:  Minimum 60.

          - Water resistant.

          - Mold and mildew resistant.

          - VOC:  Maximum 395 g/L.

          - Maximum Static-Pressure Class:  10-inch wg (2500 Pa), positive or negative.

          - Service:  Indoor or outdoor.

          - Substrate:  Compatible with galvanized sheet steel (both PVC coated and bare), stainless steel, or aluminum sheets.

- E.	Flanged Joint Sealant:  Comply with ASTM C 920.

          - General:  Single-component, acid-curing, silicone, elastomeric.

          - Type:  S.

          - Grade:  NS.

          - Class:  25.

          - Use:  O.

- F.	Flange Gaskets:  Butyl rubber, neoprene, or EPDM polymer with polyisobutylene plasticizer.

      - HANGERS AND SUPPORTS

        - Hanger Rods for Noncorrosive Environments:  Electrogalvanized steel rods and nuts.

        - Hanger Rods for Corrosive Environments:  Electrogalvanized, all-thread rods or galvanized rods with threads painted with zinc-chromate primer after installation.

        - Strap and Rod Sizes:  Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Table 4-1 (Table 4-1M), "Rectangular Duct Hangers Minimum Size," and Table 4-2, "Minimum Hanger Sizes for Round Duct."

        - Steel Cables for Galvanized-Steel Ducts:  Galvanized steel complying with ASTM A 603.

        - Steel Cables for Stainless-Steel Ducts:  Stainless steel complying with ASTM A 492.

        - Steel Cable End Connections:  Cadmium-plated steel assemblies with brackets, swivel, and bolts designed for duct hanger service; with an automatic-locking and clamping device.

        - Duct Attachments:  Sheet metal screws, blind rivets, or self-tapping metal screws; compatible with duct materials.

        - Trapeze and Riser Supports:

          - Supports for Galvanized-Steel Ducts:  Galvanized-steel shapes and plates.

          - Supports for Stainless-Steel Ducts:  Stainless-steel shapes and plates.

          - Supports for Aluminum Ducts:  Aluminum or galvanized steel coated with zinc chromate.

      - SEISMIC-RESTRAINT DEVICES

        - Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

          - Cooper B-Line, Inc.; a division of Cooper Industries.

          - Ductmate Industries, Inc.

          - Hilti Corp.

          - Kinetics Noise Control.

          - Loos & Co.; Cableware Division.

          - Mason Industries.

          - TOLCO; a brand of NIBCO INC.

          - Unistrut Corporation; Tyco International, Ltd.

- B.       Channel Support System:  Shop- or field-fabricated support assembly made of slotted steel channels rated in tension, compression, and torsion forces and with accessories for attachment to braced component at one end and to building structure at the other end.  Include matching components and corrosion-resistant coating.

- C.     Restraint Cables:  ASTM A 603, galvanized-steel cables with end connections made of

- cadmium-plated steel assemblies with brackets, swivel, and bolts designed for restraining

- cable service; and with an automatic-locking and clamping device or double-cable clips.

- D.     Hanger Rod Stiffener:  Reinforcing steel angle clamped to hanger rod.

- PART 3-EXECUTION

  - DUCT INSTALLATION

- A.       Drawing plans, schematics, and diagrams indicate general location and arrangement of duct system.  Indicated duct locations, configurations, and arrangements were used to size ducts and calculate friction loss for air-handling equipment sizing and for other design considerations.  Install duct systems as indicated unless deviations to layout are approved on Shop Drawings and Coordination Drawings.

        - Install ducts according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" unless otherwise indicated.

        - Install round and flat-oval ducts in maximum practical lengths.

        - Install ducts with fewest possible joints.

        - Install factory- or shop-fabricated fittings for changes in direction, size, and shape and for branch connections.

        - Unless otherwise indicated, install ducts vertically and horizontally, and parallel and perpendicular to building lines.

        - Install ducts close to walls, overhead construction, columns, and other structural and permanent enclosure elements of building.

        - Install ducts with a clearance of 1 inch (25 mm), plus allowance for insulation thickness.

        - Route ducts to avoid passing through transformer vaults and electrical equipment rooms and enclosures.

        - Where ducts pass through non-fire-rated interior partitions and exterior walls and are exposed to view, cover the opening between the partition and duct or duct insulation with sheet metal flanges of same metal thickness as the duct.  Overlap openings on four sides by at least 1-1/2 inches (38 mm).

        - Where ducts pass through fire-rated interior partitions and exterior walls, install fire dampers.  Comply with requirements in Division 15 Section "Duct Accessories" for fire and smoke dampers.

        - Protect duct interiors from moisture, construction debris and dust, and other foreign materials. Comply with SMACNA's "Duct Cleanliness for New Construction Guidelines."

  - SEISMIC-RESTRAINT-DEVICE INSTALLATION

- A. Install ducts with hangers and braces designed to support the duct and to restrain against

- seismic forces required by applicable building codes.  Comply with SMACNA's "Seismic

- Restraint Manual:  Guidelines for Mechanical Systems."

- Select seismic-restraint devices with capacities adequate to carry present and future static and seismic loads.

- Install cables so they do not bend across edges of adjacent equipment or building structure.

- Install cable restraints on ducts that are suspended with vibration isolators.

  - FIELD QUALITY CONTROL

        - Perform tests and inspections.

        - Leakage Tests:

- 1.Comply with SMACNA's "HVAC Air Duct Leakage Test Manual."

- 2.Test the following systems:

  - Supply air.

        - Disassemble, reassemble, and seal segments of systems to accommodate leakage testing

- and for compliance with test requirements.

        - Test for leaks before insulation application.

        - Conduct tests at static pressures equal to maximum design pressure of system or section being tested.  If static-pressure classes are not indicated, test entire system at maximum system design pressure.  Do not pressurize systems above maximum design operating pressure.

        - Duct System Cleanliness Tests:

- 1.Visually inspect duct system to ensure that no visible contaminants are present.

        - Duct system will be considered defective if it does not pass tests and inspections.

        - Prepare test and inspection reports containing the quantity of each inspection on the

- executed ductworks and its related accessories.

  - DUCT CLEANING

        - Clean new and existing duct system(s) before testing, adjusting, and balancing.

  - DUCT SCHEDULE

        - Fabricate ducts with galvanized sheet steel

        - Intermediate Reinforcement:

      - Galvanized-Steel Ducts:  Galvanized steel.

END OF SECTION

SECTION:  7.00

AIR TERMINALS

DIFFUSERS, REGISTERS, AND GRILLES

Part 1: General.

  - RELATED DOCUMENTS

- Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

  - SUMMARY

        - Section Includes:

          - Rectangular and square ceiling diffusers and wall registers & grilles.

          - Louver face diffusers.

          - Fixed face grilles.

          - Door grilles.

  - SUBMITTALS

        - Product Data:  For each type of product indicated, include the following:

          - Data Sheet:  Indicate materials of construction, finish, and mounting details; and performance data including throw and drop, static-pressure drop, and noise ratings.

          - Diffuser, Register, and Grille Schedule:  Indicate drawing designation, room location, quantity, model number, size, and accessories furnished.

        - Samples for Initial Selection:  For diffusers, registers, and grilles with factory-applied color finishes.

        - Samples for Verification:  For diffusers, registers, and grilles, in manufacturer's standard sizes to verify color selected.

        - Coordination Drawings:  Reflected ceiling plans, drawn to scale, on which the following items are shown and coordinated with each other, using input from Installers of the items involved:

          - Ceiling suspension assembly members.

          - Method of attaching hangers to building structure.

          - Size and location of initial access modules for acoustical tile.

          - Ceiling-mounted items including lighting fixtures, diffusers, grilles, speakers, access panels, and special moldings.

          - Duct access panels.

        - Source quality-control reports.

- PRODUCTS

      - MANUFACTURERS

          - Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

            - Anemostat Products; a Mestek company.

            - Carnes.

            - Hart & Cooley Inc.

            - METALAIRE, Inc.

            - Nailor Industries Inc.

            - Price Industries.

            - Titus.

            - Tuttle & Bailey.

            - KBE.

- A      Rectangular and Square Ceiling Diffusers:

- Material:  Aluminum.

          - Finish:  Anodized Aluminum.

          - Face Style:  Four cone.

          - Mounting:  Surface T-bar.

          - Pattern:  Adjustable.

          - Dampers:  Combination damper and grid.

          - Accessories:

            - Equalizing grid.

            - Plaster ring.

            - Safety chain.

            - Wire guard.

            - Sectorizing baffles.

            - Operating rod extension.

        - Louver Face Diffuser:

          - Material:  Aluminum.

          - Finish:  Anodized Aluminum.

          - Mounting:  Surface.

          - Pattern: Four-way core style.

          - Dampers:  Radial opposed blade Butterfly.

          - Accessories:

            - Square to round neck adaptor.

            - Adjustable pattern vanes.

            - Throw reducing vanes.

            - Equalizing grid.

            - Plaster ring.

            - Safety chain.

            - Wire guard.

            - Sectorizing baffles.

            - Operating rod extension.

      - REGISTERS AND GRILLES

        - Fixed Face Grille:

          - Material:  Aluminum.

          - Finish:  Baked enamel, color selected by The Engineer.

          - Face Arrangement:  Perforated core.

          - Mounting:  Concealed.

          - Accessory:  Filter.

        - Door Grille:

          - Material: Aluminum.

          - Finish: Baked enamel, color selected by the Engineer.

          - Face Arrangement: Horizontal.

          - Monitoring: Counter sunk screw.

      - SOURCE QUALITY CONTROL

        - Verification of Performance: Rate diffusers, registers, and grilles according to ASHRAE 70, "Method of Testing for Rating the Performance of Air Outlets and Inlets."

- EXECUTION

      - EXAMINATION

        - Examine areas where diffusers, registers, and grilles are to be installed for compliance with requirements for installation tolerances and other conditions affecting performance of equipment.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - INSTALLATION

        - Install diffusers, registers, and grilles level and plumb as shown on the drawings.

        - Ceiling-Mounted Outlets and Inlets: Drawings indicate general arrangement of ducts, fittings, and accessories.  Air outlet and inlet locations have been indicated to achieve design requirements for air volume, noise criteria, airflow pattern, throw, and pressure drop.  Make final locations where indicated, as much as practical. For units installed in lay-in ceiling panels, locate units in the center of panel. Where architectural features or other items conflict with installation, notify The Engineer for a determination of final location.

        - Install diffusers, registers, and grilles with airtight connections to ducts and to allow service and maintenance of dampers, air extractors, and fire dampers.

        - Color and paint of air outlets as directed by the Engineer.

      - ADJUSTING

        - After installation, adjust diffusers, registers, and grilles to air patterns indicated, or as directed, before starting air balancing.

END OF SECTION

SECTION:  8.00

###### FIRE PROTECTION SYSTEMS

# PART 1   GENERAL

This section covers requirements for Fire Fighting System. It included, fire fighting piping network, fire hydrants, fire hose cabinets and fire extinguishing equipment. For fire pumps, refer to relevant section Fire Pumps.

1.1   	GENERAL REQUIREMENTS

This section covers specifications for fire protection works, which include fire yard hydrants system, hose reel system and automatic helipad fire fighting system as indicated on design drawings. The fire fighting pumping station is located in the underground pump room and its specifications are included in relevant section for fire pumps.

1.2   	COORDINATION OF TRADES

Piping offsets, fittings, and any other accessories required shall be furnished as required to provide a complete installation and to eliminate interference with other construction.

1.3   	FIELD MEASUREMENTS

The Contractor shall become familiar with all details of the work, verify all dimensions in the field, and shall advise the Contracting Officer of any discrepancy before performing the work.

1.4   	SUBMITTALS

"CDD" indicates that Civil Defence approval is required for the related submittal. Where CDD approval is required, submittals shall be approved by the Civil Defence Department before being submitted to the Engineer.

Shop Drawings

As-Built Shop Drawings, CDD

Product Data

Fire Protection Related Submittals, CDD

Components and Equipment Data, CDD

Hydraulic Calculations, CDD

Hydraulic calculations, including a drawing showing hydraulic reference points and pipe segments.

Preliminary Tests Procedures

Proposed procedures for Preliminary Tests, no later than 14 days prior to the proposed start of the tests.

Final Acceptance Test Procedures, CDD

Proposed procedures for Final Acceptance Test, no later than 14 days prior to the proposed start of the tests.

Preliminary Tests.

Proposed date and time to begin Preliminary Tests, submitted with the Preliminary Tests Procedures.

Final Acceptance Test, CDD

Proposed date and time to begin Final Acceptance Test, submitted with the Final Acceptance Test Procedures.  Notification shall be provided at least 14 days prior to the proposed start of the test.  Notification shall include a copy of the Contractor's Material & Test Certificates.

Test Reports

Preliminary Tests Report.

Three copies of the completed Preliminary Tests Reports, no later that 7 days after the completion of the Preliminary Tests. The Preliminary Tests Report shall include both the Contractor's Material and Test Certificate for Underground Piping and the Contractor's Material and Test Certificate for Aboveground Piping. All items in the Preliminary Tests Report shall be signed by the Fire Protection Specialist.

Final Acceptance Test Report, CDD

Three copies of the completed Final Acceptance Tests Reports, no later that 7 days after the completion of the Final Acceptance Tests.  All items in the Final Acceptance Report shall be signed by the CDD officer.

1.5   	REGULATORY REQUIREMENTS

Compliance with referenced NFPA, as well as, CDD standards is mandatory.  This includes advisory provisions listed in the appendices of such standards, as though the word "shall" had been substituted for the word "should" wherever it appears.  In the event of a conflict between specific provisions of this specification and applicable NFPA standards, this specification shall govern.  Reference to "authority having jurisdiction" shall be interpreted to mean the CDD Officer.

# PART 2   PRODUCTS

2.1   	STANDARD PRODUCTS

Materials and equipment shall be standard products of a manufacturer regularly engaged in the manufacture of such products and shall essentially duplicate items that have been in satisfactory use for at least 2 years prior to bid opening.

2.2   	NAMEPLATES

All equipment shall have a nameplate that identifies the manufacturer's name, address, type or style, model or serial number, and catalog number.

2.3   	REQUIREMENTS FOR FIRE PROTECTION SERVICE

All Materials and Equipment shall be CDD approved.

2.4   	UNDERGROUND PIPING COMPONENTS

2.4.1   	Pipe

All pipes shall be ductile iron with a rated working pressure of 1207 kPa conforming to AWWA C151, with cement mortar lining conforming to AWWA C104.

2.4.2   	Fittings and Gaskets

Fittings shall be ductile iron conforming to AWWA C110. Gaskets shall be suitable in design and size for the pipe with which such gaskets are to be used.  Gaskets for ductile iron pipe joints shall conform to AWWA C111.

2.4.3   	Gate Valve and Indicator Posts

Gate valves for underground installation shall be of the inside screw type with counter-clockwise rotation to open. Where indicating type valves are shown or required, indicating valves shall be gate valves with an approved indicator post of a length to permit the top of the post to be located 900mm above finished grade. Gate valves and indicator posts shall be listed in UL Fire Prot Dir or FM P7825a and FM P7825b.

2.5   	ABOVEGROUND PIPING COMPONENTS

Aboveground piping shall be steel.

2.5.1   	Steel Piping Components

2.5.1.1 Steel Pipe

Except as modified herein, steel pipe shall be black as permitted by NFPA 13 and shall conform to provisions of ASTM A 53/A 53M.  Pipe in which threads or grooves are cut shall be Schedule 40 or shall be listed by Underwriters' Laboratories to have a corrosion resistance ratio (CRR) of 1.0 or greater after threads or grooves are cut.  Pipe shall be marked with the name of the manufacturer, kind of pipe, and ASTM designation.

2.5.1.2 Fittings for Non-Grooved Steel Pipe

Fittings shall be cast iron conforming to ASME B16.4, steel conforming to ASME B16.9 or ASME B16.11, or malleable iron conforming to ASME B16.3. Steel press fittings shall be approved for fire protection systems.  Galvanized fittings shall be used for piping systems or portions of piping systems utilizing galvanized piping. Plain-end fittings with mechanical couplings, fittings that use steel gripping devices to bite into the pipe and segmented welded fittings shall not be used.

2.5.1.3 Grooved Mechanical Joints and Fittings

Joints and fittings shall be designed for not less than 1200 kPa service and shall be the product of the same manufacturer.  Fitting and coupling houses shall be malleable iron conforming to ASTM A 47/A 47M, Grade 32510; ductile iron conforming to ASTM A 536, Grade 65-45-12.  Gasket shall be the flush type that fills the entire cavity between the fitting and the pipe.  Nuts and bolts shall be heat-treated steel conforming to ASTM A 183 and shall be cadmium plated or zinc electroplated.

2.5.1.4 Flanges

Flanges shall conform to NFPA 13 and ASME B16.1. Gaskets shall be non asbestos compressed material in accordance with ASME B16.21, 1.6mm thick, and full face or self-centering flat ring type.  Bolts shall be square head conforming to ASME B18.2.1 and nuts shall be hexagon type conforming to ASME B18.2.2.

2.5.2   	Pipe Hangers

Hangers shall be listed in UL Fire Prot Dir or FM P7825a and FM P7825b and of the type suitable for the application, construction, and pipe type and sized to be supported.

2.5.3   Valves

2.5.3.1   Control Valve and Gate Valve

Manually operated control valve and gate valve shall be outside stem and yoke (OS&Y) type and shall be listed in UL Bld Mat Dir or FM P7825a and FM P7825b.

2.5.3.2   Check Valve

Check valve 50mm and larger shall be listed in UL Bld Mat Dir or FM P7825a and FM P7825b. Check valves 100mm and larger shall be of the swing type with flanged cast iron body and flanged inspection plate, shall have a clear waterway and shall meet the requirements of MSS SP-71, for Type 3 or 4.

2.5.3.3   Hose Valve

Valve shall comply with UL 668 and shall have a minimum rating of 2070 kPa. Valve shall be non-rising stem, all bronze, 90 degree angle type, with 65mm American National Standard Fire Hose Screw Thread (NH) male outlet in accordance with NFPA 1963. Hose valves shall be equipped with lugged cap with drip drain, cap gasket and chain. Valve finish shall be polished brass.

2.6   	PEDESTAL FIRE HYDRANTS

Hydrants shall be of CDD approved type and shall have not less than a 150mm diameter connection with the mains. Yard post hydrants shall have valve housings located below frost lines. The hydrants shall have two independent 65mm outlets with two independent isolating valves. Hydrant outlet threads shall have NH standard external threads. Water from the casing shall be drained after valve is shut off. Hydrant shall be bronze with cast-iron box or casing guard. "T" handle key shall be provided. Each fire hydrant shall be supplied with two standard 65mm fire hose in adequate hose house located immediately nearby each hydrant. The hose shall standard fire hose conforming to NFPA 1961, and shall be minimum 45 meters long. The coupling threads on the hose connectors shall be standard NH threads to NFPA 1963. In addition to the fire hose, each hose house shall be equipped with:

a. 	2 hose coupling gaskets for each size house

b. 	4 coupling spanners for each size hose provided

c. 	2 hydrant wrenches

d. 	2 approved adjustable spray-solid stream nozzles equipped with shutoffs for each size of hose provided.

2.7   	FIRE HOSE REEL ASSEMBLY AND FIRE HOSE CABINET

The fire hose cabinet shall be automatic swinging recessed type as shown on drawings. Hose reels shall be in accordance with BS 5274. The hose reel shall have a 30 meters long of 25mm. internal diameter reinforced non-kinkable rubber hose capable of withstanding a working pressure of 16 bar. The hose shall be wound on a fabricated steel drum with circular side plates. The hose reel shall turn on automatically when 1.5-1.8 meters of hose is withdraw from the real. The hose reel shall be equipped with shut-off valve for connecting with pipework. The hose reel shall also be equipped with pressure reducing valve to drop pressure from designated pressure of main pipe to 3.0 bar. The hose nozzle shall be of high impact plastic, JET/SPRAY/SHUT/OFF nozzle. The cabinet shall be heavy steel construction finished with red colour paint labelled "FIRE HOSE REEL" and in Arabic. The fire hose cabinet shall include a 9 Kg dry chemical fire extinguisher of the ABC type as specified hereafter. The fire hose cabinet shall be of dimensions sufficient to include the hose reel, the shut-off valve and the fire extinguisher and to fit with the available space as shown on the Drawings. The unit price shall include hose reel, 9 Kg dry chemical portable fire extinguisher of the ABC type, pressure reducing valve, globe valve and cabinet as detailed on drawings.

2.8   	Portable Fire Extinguishers

The fire extinguishers shall be of the rechargeable type and shall be supplied complete with the operating charge from the factory. All portable fire extinguishers shall be mounted by suitable wall bracket or in a recessed cabinets as instructed by the engineer. The bracket and cabinet shall be specifically supplied for the extinguisher type and size concerned. All fire extinguishers shall have a capacity of 9 kg.

Dry chemical fire extinguishers shall be of the ABC type with a rugged all-brass operating valve, large size operating lever, full vision pressure gauge, discharge hose and heavy duty drawn steel cylinder with hard, scratch resistant finish.

# PART 3 EXECUTIONS

3.1   	INSTALLATION REQUIREMENTS

The installation shall be in accordance with the applicable provisions of NFPA 13, NFPA 14, NFPA 24 and publications referenced therein.

3.2   	ABOVEGROUND PIPING INSTALLATION

3.2.1   Piping in Exposed Areas

Exposed piping shall be installed so as not to diminish exit access widths, corridors or equipment access.  Exposed horizontal piping, including drain piping, shall be installed to provide maximum headroom.

3.2.2   	Piping in Finished Areas

In areas with suspended or dropped ceilings and in areas with concealed spaces above the ceiling, piping shall be concealed above ceilings. Piping shall be inspected, tested and approved before being concealed. Risers and similar vertical runs of piping in finished areas shall be concealed.

3.2.3   	Pipe Joints

Pipe joints shall conform to NFPA 13, except as modified herein. Not more than four threads shall show after joint is made up. Welded joints will be permitted, only if welding operations are performed as required by NFPA 13 at the Contractor's fabrication shop, not at the project construction site. Flanged joints shall be provided where indicated or required by NFPA 13. Grooved pipe and fittings shall be prepared in accordance with the manufacturer's latest published specification according to pipe material, wall thickness and size. Grooved couplings and fittings shall be from the same manufacturer.

3.2.4   	Reducers

Reductions in pipe sizes shall be made with one-piece tapered reducing fittings.  The use of grooved-end or rubber-gasketed reducing couplings will not be permitted. When standard fittings of the required size are not manufactured, single bushings of the face type will be permitted. Where used, face bushings shall be installed with the outer face flush with the face of the fitting opening being reduced. Bushings shall not be used in elbow fittings, in more than one outlet of a tee, in more than two outlets of a cross, or where the reduction in size is less than 15 mm.

3.2.5   	Pipe Penetrations

Cutting structural members for passage of pipes or for pipe-hanger fastenings will not be permitted. Pipes that must penetrate concrete or masonry walls or concrete floors shall be core-drilled and provided with pipe sleeves. Each sleeve shall be Schedule 40 galvanized steel, ductile iron or cast iron pipe and shall extend through its respective wall or floor and be cut flush with each wall surface. Sleeves shall provide required clearance between the pipe and the sleeve per NFPA 13. The space between the sleeve and the pipe shall be firmly packed with mineral wool insulation. Where pipes penetrate fire walls, fire partitions, or floors, pipes shall be fire stopped. In penetrations that are not fire-rated or not a floor penetration, the space between the sleeve and the pipe shall be sealed at both ends with plastic waterproof cement that will dry to a firm but pliable mass or with a mechanically adjustable segmented elastomer seal.

3.3   	UNDERGROUND PIPING INSTALLATION

The fire protection water main shall be laid, and joints anchored, in accordance with NFPA 24. Minimum depth of cover shall be 1000mm. The supply line shall terminate inside the building with a flanged piece, the bottom of which shall be set not less than 150mm above the finished floor. A blind flange shall be installed temporarily on top of the flanged piece to prevent the entrance of foreign matter into the supply line. A concrete thrust block shall be provided at the elbow where the pipe turns up toward the floor. In addition, joints shall be anchored in accordance with NFPA 24 using pipe clamps and steel rods from the elbow to the flange above the floor and from the elbow to a pipe clamp in the horizontal run of pipe.

3.4   	EARTHWORK

Earthwork shall be performed in accordance with applicable provisions of related sections.

3.5   	PIPE COLOR CODE MARKING

Color code marking of piping shall be red color for all fire piping in accordance with related sections for painting.

3.6   	PRELIMINARY TESTS

The system, including the underground water mains, and the aboveground piping and system components, shall be tested to assure that equipment and components function as intended. The underground and aboveground interior piping systems and attached appurtenances subjected to system working pressure shall be tested in accordance with NFPA 13 and NFPA 24.

3.6.1   	Underground Piping

3.6.1.1   Flushing

Underground piping shall be flushed in accordance with NFPA 24. This includes the requirement to flush the lead-in connection to the fire protection system at a flow rate not less that the calculated maximum water demand rate of the system.

3.6.1.2   Hydrostatic Testing

Underground piping shall be hydrostatically tested in accordance with NFPA 24.  The allowable leakage shall be measured at the specified test pressure by pumping from a calibrated container. The amount of leakage at the joints shall not exceed 1.89 liters per hour per 100 gaskets or joints, regardless of pipe diameter.

3.6.2   	Aboveground Piping

3.6.2.1   Hydrostatic Testing

Aboveground piping shall be hydrostatically tested in accordance with NFPA 13 at not less than 350 kPa in excess of maximum system operating pressure and shall maintain that pressure without loss for 2 hours. There shall be no drop in gauge pressure or visible leakage when the system is subjected to the hydrostatic test. The test pressure shall be read from a gauge located at the low elevation point of the system or portion being tested.

3.7   	FINAL ACCEPTANCE TEST

Final Acceptance Test shall begin only when the Preliminary Test Report has been approved. The Fire Protection Officer shall conduct the Final Acceptance Test and shall provide a complete demonstration of the operation of the system. In addition, the CDD representative shall have available copies of as-built drawings and certificates of tests previously conducted. The installation shall not be considered accepted until identified discrepancies have been corrected and test documentation is properly completed and duelly stamped by CDD.

3.8   	ON-SITE TRAINING

The Fire Protection Specialist shall conduct a training course for operating and maintenance personnel as designated by the Engineer. Training shall be provided for a period starting after the system is functionally complete but prior to the Preliminary Tests and Final Acceptance Test. The On-Site Training shall cover all of the items contained in the approved Operating and Maintenance Instructions.

End Of Section

SECTION:  9.00

###### FIRE PUMPS

PART 1 GENERAL

This section covers centrifugal pumps used for Fire Fighting.

1.1   	SUBMITTALS

"CDD" indicates that Civil Defence approval is required for the related submittal. Where CDD approval is required, submittals shall be approved by the Civil Defence Department before being submitted to the Engineer.

The following shall be submitted in accordance with relevant section for General Requirements and Conditions:

Shop Drawings

Installation, CDD

Product Data

Materials and Equipment, CDD

Instructions

Training Period

Test Reports

Tests, CDD

Operation and Maintenance Data

1.2   	GENERAL REQUIREMENTS

1.2.1   Standard Products

Material and equipment shall be the standard products of a manufacturer regularly engaged in the manufacture of such products and shall essentially duplicate equipment that has been in satisfactory waterworks operation at least 2 years prior to bid opening. Equipment shall be supported by a service organization that is, in the opinion of the Engineer, reasonably convenient to the jobsite. Pumps, motors and engines of the same types shall each be the product of one manufacturer.

1.2.2   	Description

The pumps shall be horizontal and vertical centrifugal water pumps of the types indicated and specified. The single or dual driving units for the pumps shall be electric motors and diesel engines as indicated and specified. On dual drive units, each type of drive shall be equipped with an approved free-wheeling clutch.

1.2.3   	Governing Requirements

Fire pumps and appurtenances shall conform in all respects to NFPA 20.

1.2.4   	Safety Requirements

Gears, couplings, projecting set-screws, keys, and other rotating parts, so located that any person can come in close proximity thereto, shall be fully enclosed or properly guarded.

1.2.5   	Nameplates

Pumps and motors shall have a standard nameplate securely affixed in a conspicuous place showing the manufacturer's name, address, type or style, model, serial number, and catalog number. In addition, the nameplate for each pump shall show the capacity in liters per second (gpm) at rated speed in rpm and head in millimeters (feet) of water. Nameplate for each electric motor shall show at least the minimum information required by 10.38 NEMA MG 1. Such other information as the manufacturer may consider necessary to complete identification shall be shown on the nameplate.

1.2.6   	Electrical Work

Electrical motor driven equipment specified herein shall be provided complete with motors, motor starters, and controls.  Electric equipment and wiring shall be in accordance with relevant Section ELECTRICAL WORK, INTERIOR. Electrical characteristics shall be as indicated. Equipment for control of automatic fire pumps shall be in accordance with NFPA 20. Motor starters shall be provided complete with properly sized thermal overload protection in each phase and other appurtenances necessary for the motor control specified.  Each motor shall be of sufficient capacity to drive the equipment at the specified capacity without exceeding the nameplate rating of the motor when operating at proper electrical system voltage and frequency. Manual or automatic control and protective or signal devices required for the operation herein specified and any control wiring required for controls and devices but not shown on electrical plans shall be provided under this section of the specifications.

1.2.7   	Selection Criteria

Pumps shall be designed using hydraulic criteria based upon actual model developmental test data. Pumps shall be selected at a point within the maximum efficiency for a given impeller casing combination. Deviations within 3 percent of maximum efficiency are permissible, provided the lesser efficiency is not less than the scheduled efficiency. Pumps having impeller diameters larger than 90 percent of the published maximum diameter of the casing or less than 15 percent larger than the published minimum diameter of the casing will be rejected. Acceptable maximum impeller diameter calculations shall not be based on percentage of impeller diameter range for a given casing.

1.2.8   	Conformance With Agency Requirements

Where materials or equipment are specified to be an approved type, the seal or label of approval from a nationally recognized testing agency, adequately equipped and competent to perform such services shall be attached thereto. A written certificate from the testing agency shall accompany the materials or equipment and shall be submitted to the Engineer stating that the items have been tested and that they conform to the applicable requirements of the specifications and to the standards listed herein. The certificate shall indicate the methods of testing used by the testing agency. In lieu of a certificate from a testing agency, published catalog specification data, accompanied by the manufacturer's certified statement to the effect that the items are in accordance with the applicable requirements of the specifications and the referenced standards, will be considered by the Engineer and may be acceptable as evidence that the items conform with agency requirements.

1.2.9   	Verification of Dimensions

The Contractor shall become familiar with all details of the work, verify all dimensions in the field and shall advise the Contracting Officer of any discrepancy before performing the work.

1.2.10   Factory Tests

Pumps shall be tested by the manufacturer or a nationally recognized testing agency in compliance with Hydraulic Institute Standards. Where two or more identical pumps are specified, only one representative pump shall be tested.  Certified test results shall be submitted to the Engineer.

PART 2   PRODUCTS

2.1   	MATERIALS AND EQUIPMENT

Materials and equipment shall be as specified below and as shown, and shall be suitable for the service intended. Materials and equipment shall be new and unused, except for tests. Where two or more pieces of equipment performing the same function are required, they shall be duplicate products of the same manufacturer.

2.2   	CENTRIFUGAL WATER PUMPS

The pumps shall be the centrifugal, single-stage or multi-stage type, designed for waterworks service as per schedule of equipment.

2.2.1   	Pump Service

The pumps shall be utilized for the indicated services as per schedule of equipment

2.2.2   	Pump Drives

The pumps shall have Electric Motors or Diesel Engine driving units as indicated on schedule of equipment and shall be directly connected to the driving units through solid shafts, flexible couplings, or free wheeling clutches (as appropriate).

2.2.3   	Pump Construction

Except, as below specified, centrifugal water pumps including required priming equipment shall be constructed in accordance with the Hydraulic Institute HI1.1-1.5. Additionally, fire pumps shall be constructed in accordance with NFPA 20 and UL 448.

2.2.4   	Pump Characteristics

The pumps shall be capable of discharging quantities at total discharge heads measured at the discharge flange, as specified in the schedule of equipment

Pumps shall operate at optimum efficiencies to produce the most economical pumping system under the conditions encountered and shall be sized to make optimum match with the system head curve as indicated. Pumps shall furnish not less than 150 percent of rated capacity at a total discharge head of not less than 65 percent of total rated head. For fire pumps, the shutoff total head shall be not greater than 120 percent of total rated head.

2.2.5   	Pump Casings

Pump casings shall be cast iron of the shaft design as indicated on the schedule of equipment

The casings shall be designed to permit replacement of wearing parts. Horizontal-split casings shall have the suction and discharge nozzles cast integrally with the lower half, so that the upper part of the casings may be removed for inspection of the rotating parts without disturbing pipe connections or pump alignment. Pump casings shall be of uniform quality and free from blowholes, porosity, hard spots, shrinkage defects, cracks and other injurious defects. Defects in casings shall not be repaired except when such work is approved and is done by or under the supervision of the pump manufacturer, and then only when the defects are small and do not adversely affect the strength or use of the casing. Casings shall be single or double volute with flanged piping connections conforming to ASME B16.1, Class 125. The direction of shaft rotation shall be conspicuously indicated. The casing shall have tapped openings for air venting, priming, draining, and suction and discharge gauges.  A brass or bronze umbrella or vent cock shall be furnished for venting except where automatic air vents are indicated. Drain openings in the volute, intake, or other passages capable of retaining trapped water shall be located in the low point of such passages.

2.2.6   	Impellers

Impellers shall be of enclosed design and shall be constructed of Stainless Steel, carefully finished with smooth water passageways, and shall be statically and dynamically balanced. Impellers shall be securely keyed to the pump shaft.  Provisions shall be made for vertical impeller adjustment at the top of the motor.

2.2.7   	Wearing Rings

Wearing rings of Stainless Steel shall be provided for impellers. Wearing rings of a different composition or of a suitable ferrous material shall be provided for pump casings. Casing rings shall be securely fixed in position to prevent rotation.  Rings shall be renewable and designed to ensure ease of maintenance.

2.2.8   	Shaft

Shaft shall be of Stainless steel, accurately machined, and shall be of sufficient size and strength to perform the work required. Vertical shafts shall be the open type and shall be adequately provided with alignment bearings. Stainless Steel renewable shaft sleeves shall be provided for protection of the shaft in contact with water, and in the stuffing boxes. Shaft sleeves shall be keyed to the pump shaft.

2.2.9   	Mechanical Seals

Mechanical seals shall be balanced or unbalanced, as necessary to conform to specified service requirements. Mechanical seals shall be constructed in a manner and of materials particularly suitable for the temperature service range and quality of water being pumped. Seal construction shall not require external source cooling for pumped-fluid service temperatures up to 120 degrees C. Seal pressure rating shall be suitable for maximum system hydraulic conditions.  Materials of construction shall include AISI 300 series stainless steel, solid tungsten-carbide rotating-seal face, and Buna-N vinylidene-fluoride-hexafluoropropylene, EPT, or tetrafluoroethylene seals. Bypass flushing water supply shall be free of iron rust products and other abrasive materials and shall be directed onto face of seal without dead ending. All piping and accessories shall be provided. Throttling bushing shall have clearances to minimize leakage in case of complete seal failure without restriction of flushing water. Mechanical seals shall not be subjected to hydrostatic test pressures in excess of the manufacturer's recommendations.

2.2.10   Couplings

Couplings shall be of the heavy-duty flexible type, keyed and locked to the shaft.  The outside surface of the couplings for horizontal pumps and close-coupled vertical pumps shall be machined parallel to the axis of the shaft. The faces of the couplings shall be machined perpendicular to the axis of the shaft.  Disconnecting the couplings shall be accomplished without removing the driver half or the pump half of the couplings from the shaft. Couplings for vertical pumps other than close-coupled vertical pumps may be of the universal type.  Flexible couplings shall not be used to compensate for misalignment of pump.

2.2.11   Balance

All rotating parts of the equipment shall operate throughout the required range without excessive end thrust, vibration, or noise. Defects of this type that cannot be eliminated by installation adjustments will be sufficient cause for rejection of the equipment. Pump impeller assemblies shall be statically and dynamically balanced to within 1/2 percent of W times R squared, where W equals weight and R equals impeller radius. Shaft construction shall be substantial to prevent seal or bearing failure due to vibration. Total shaft peak-to-peak dynamic deflection measured by vibro meter at pump-seal face shall not exceed 0.051 mm (2.0 mils) under shutoff-head operating conditions. Flow from 8 mm (1/4 inch) iron pipe size (ips) pipe shall be provided during testing.

2.2.12   Bearings

Bearings shall be ball or roller type, and the main bearings shall take all radial and end thrust.  Pumps that depend only on hydraulic balance to overcome end thrust will not be acceptable.

2.2.13   Lubrication

Bearings on horizontal-shaft pumps shall be either oil-bath type or grease type.  Each oil reservoir shall be liberal in size and provided with an opening for filling, an overflow opening at the proper location to prevent overfilling, an oil-level sight glass, and a drain at the lowest point. Bearings on vertical shaft wet-pit pumps shall be either oil or water type. Pumps with oil-lubrication systems shall be designed so that all shaft bearings will be isolated from the pumped liquid.  An automatic sight feed oiler shall be provided on a suitable mounting bracket with connection to the shaft tube. Bearings on vertical-shaft dry-pit pumps shall be grease type. Grease type bearings shall be provided with fittings for a grease gun and, if the bearings are not easily accessible, with grease tubing extending to convenient locations. The grease fittings shall be of a type that prevent over lubrication and the buildup of pressure injurious to the bearings.

2.2.14   Base Plates

Horizontal-shaft centrifugal pumps shall be provided with a common base for mounting each pump and driving unit of the pump on the same base. Each base shall be constructed of cast iron with a raised lip tapped for drainage, or of welded steel shapes with suitable drainage pan. Horizontal-shaft end suction pumps shall be mounted on a factory furnished channel steel frame. With the exception of close-coupled pumps, horizontal-shaft end suction pumps shall be frame mounted. Vertical-shaft pumps shall be provided with complete mounting suitable for the type of pump furnished, with the base for the pump separate from the base of the driving unit. The drainage structure shall collect the packing box leakage and shall have a 15mm (1/2 inch) NPT connection to connect it to a drain.

2.2.15   Cocks, Plugs, and Accessories

The pumps shall be equipped with air cocks, drain plugs, and single gauges indicating discharge pressures for all pumps and suction pressures for pumps without suction lift. Gauges, equipped with a shutoff cock and snubber, shall conform to ASME B40.1, and shall be calibrated in kilopascals and pounds per square inch in not more than 10 kPa and 2 psi increments. Gauge ranges shall be appropriate for the particular installation. Normal operating suction and discharge pressures of the pump shall be indicated on the mid-point range of the gauges. Pressure relief valve shall be furnished and installed where indicated. Suction lift pipe shall be provided with a foot valve as shown, capable of preventing loss of prime when the pump rotation is stopped.

2.2.16   Piping Connections

The pump suction and discharge shall be provided with flanged connections of suitable size and suitably arranged for piping shown. Pipe flanges shall conform to ASME B16.1 and ASME B16.5. Piping shall be installed to preclude the formation of air pockets.

2.2.17   Finish

Pump shall have painted or enameled finish as is standard with the manufacturer except that fire pumps shall be red in color.

2.3   	ELECTRICAL EQUIPMENT

Electrical equipment shall conform to relevant Section in Electrical Specifications.  Electrical motor driven equipment herein specified shall be provided complete with motors, motor starters, and controls.  Motor controls, equipment, and wiring shall be in accordance with NFPA 70.

2.3.1   Electric Motors

Each electric motor-driven pump shall be driven by a weather-protected, Type I continuous-duty electric motor. Motors shall be squirrel-cage induction motors having normal-starting-torque and low-starting-current characteristics, and shall be of sufficient size so that the nameplate horsepower rating will not be exceeded throughout the entire published pump characteristic curve. Motor bearings shall provide smooth operations under the conditions encountered for the life of the motor. Adequate thrust bearing shall be provided in the motor to carry the weight of all rotating parts plus the hydraulic thrust and shall be capable of withstanding up thrust imposed during pump starting and under variable pumping head conditions specified.  Motors shall be rated as specified in schedule of equipment and such rating shall be stamped on the nameplate.  Motors for fire pumps shall conform to NFPA 20.  Motors, not driving fire pumps, shall conform to NEMA MG 1.

2.3.2   	Control Equipment

Automatically controlled pumps shall have three-position "MANUAL-OFF-AUTOMATIC" selector switch in cover. Additional controls or protective devices shall be as indicated. Control equipment for fire pumps shall conform to NFPA 20. A pump low-water cutoff shall be installed on the suction pipe and shall shut the pump off when the water level in the well reaches the level indicated on drawings.

2.4   	DIESEL ENGINES

Diesel engines shall be water-cooled, heavy duty, compression-ignition, cold-starting engines with removable cylinder sleeves. Engines may be 2-cycle or 4-cycle and may be either naturally aspirated, scavenged or turbocharged and shall operate satisfactorily on No. 2D diesel fuel conforming to ASTM D 975. Engines shall be provided with a manual clutch and arranged for connection to the pump through a flexible shaft with a splined joint. Engines shall be current models of a type in regular production and shall be complete with all devices specified and normally furnished with the engine. Engines shall have a published continuous horsepower rating at least 20 percent greater than that required at any point on the pump performance curve at the specified pump speed plus power required for any engine driven accessories. Naturally aspirated ratings shall be decreased by 3 percent for every 300 m of altitude, and 1 percent for every 5 degrees C that the engine performance conditions exceed the published rating conditions.  Scavenged or turbocharged engine ratings shall be decreased as indicated by the engine manufacturer's engine performance data. Engine shall be suitable for performance at 15 degrees C (59 degrees F) ambient and 800m elevation. Engine speed shall not exceed 1,800 rpm when driving the pump at rated conditions. Engines driving fire pumps shall conform to NFPA 20. Engines shall be capable of starting and assuming full load within 10 to 15 seconds, with a minimum ambient temperature of 0degrees C (32 degrees F).  Approved engine jacket water and lube oil heaters shall be provided as recommended by the manufacturer.  Lube oil heaters shall be of the circulation type.

2.5   	ENGINE EQUIPMENT AND ACCESSORIES

2.5.1   	Governor

Engine shall be equipped with an adjustable constant speed governor set to maintain pump speed within 3 percent of rated speed at rated load. A separate, manual reset, overspeed device shall be provided which shall shut down the engine in the event the speed reaches approximately 15 percent above rated speed.

2.5.2   	Cooling System

Cooling system shall be the forced-circulation, closed type and shall include a fan and an engine mounted radiator. Radiator shall be of sufficient capacity to operate the engine at full rated load at 0-50 degrees C ambient temperatures.  Closed jacket water circuit shall be thermostatically controlled, and shall include an integral circulating pump. Drain cocks shall be provided at low points of the closed jacket water system. Exhaust manifolds shall be water jacketed or provided with an insulating jacket furnished by the engine manufacturer. Engine cooling system shall be charged with an inhibited ethylene-glycol solution to provide antifreeze protection to-10 degrees C.

2.5.3   	Lubrication

Engine lubrication shall be a pressure circulation system with an engine driven pump and engine mounted oil cooler. Full flow type filters with automatic bypass or bypass type filters shall be provided. Filter elements shall be of replaceable type and shall be readily accessible.

2.5.4   	Exhaust System

Engine exhaust system shall be equipped with a residential type silencer with drains and flexible, stainless steel connection. Flexible connector shall be provided with factory fabricated expanded metal personnel protection guards.  Silencers shall be mounted inside and shall be of the straight through, or side inlet type as required to suit the space available and the engine exhaust arrangement. An engine with dual exhaust outlets and provided with one exhaust silencer shall have dual inlets on the silencer or a factory fabricated Y-branch or equivalent fitting to join the two exhausts together.

2.5.5   	Air Intake Equipment

Each engine shall be provided with a dry cleanable type intake air cleaner.  Filter shall be engine mounted.

2.5.6   	Starting Equipment

Engine shall be provided with an electric starting motor suitable for the starting service specified.

2.5.7   	Batteries

Each engine shall be provided with heavy-duty nickel-cadmium alkline or lead acid type starting batteries. Batteries shall have sufficient capacity at 0 degrees C (32 degrees F) to provide the necessary cranking speed through 20 minutes of cranking cycles specified. Batteries shall be provided with a battery rack, and if material is not inherently resistant to acid, coating shall be applied to the stand.  Connecting cables shall be provided as required. A dual battery set sized to NFPA 20 requirements with rack and cables shall be provided for fire service systems.

2.5.8   	Battery Charging

Engine shall be equipped with an engine driven battery charging alternator with a regulator for use when the engine is running. A separately mounted battery charger shall also be furnished.  Battery charger shall be an automatic, float type providing continuous taper charging. Output characteristics shall match the requirements of the battery furnished. Charger shall be suitable for operation and shall be rated not less than 6 amperes dc. A dual battery charger of proper type for batteries used shall be provided for fire service systems. Where wall mounting is indicated, enclosure shall be suitable for conduit connection, and ventilating openings shall be guarded.  An interlock is required between the engine driven charging system and the charger. Battery charger shall have the following features:

a.  	Direct gulation shall be within plus or minus 2 percent for variations in line voltage of plus or minus 10 percent.

b.  	Direct current voltmeter and direct current ammeter, each with numerical scales.

c.  	Automatic surge suppressor.

d.  	Automatic current limiting to prevent overloading due to engine cracking, shorted output or reversed battery connections.

e.  	Alternating current line fusing.

f.  	Equalize charge rate with manually set timer.

g.  	Integral protection to prevent battery discharge through the charger on loss of alternating current line voltage.

h.  	Terminal block with terminals for all external connections.

2.5.9   	Safety Controls

Each engine shall be equipped with automatic shut down features to stop the engine for high jacket water temperature, low oil pressure, and engine overspeed. Shutdown features shall be connected to the annunciator on the instrument panel and each shutdown feature will be identified.

2.5.10   Instrument Panel

Each engine shall be furnished with an instrument panel mounted with vibration isolators on the unit.  Instruments shall be of the direct reading type and shall be factory mounted &connected. Panel shall include the following features &  instruments:

a.  	Three-position MANUAL-OFF-AUTO switch.

b.  	Manual starting switch.

c.  	Water temperature gauge.

d.  	Ammeter-charging circuit.

e.  	Tachometer.

f.  	Lubricating oil pressure gauge.

g.  	Running time meter.

h.  	Alarm annunciator with single audible alarm and with contacts to operate a remote alarm and individual indicating lights for low-oil pressure, high-water temperature, engine overspeed, and failure of engine to start.

i.  	Manual engine speed regulating device.

j.  	Additional instruments or devices that are required for use in conjunction with the engine controls specified.

k.  	Auxiliary contacts.

2.5.11  Engine Control

2.5.11.1   Single Units

Each engine shall be manually started by a pushbutton switch on the engine instrument panel through a suitably enclosed relay. Cyclic operation of the motor shall not be provided. Each engine shall be automatically started by a pilot-control circuit. A control panel enclosing all relays, contactors, and timers shall be mounted on the wall. Panel shall be provided with hinged cover and latch. Engine starting circuit shall provide for 3 or 4 interrupted cranking periods of approximately 15 seconds with equal rest periods between, unless the engine starts before the end of that time.  At the end of the period, the starter circuit shall be de-energized. Starter motor shall be automatically de-energized when the engine starts. Engines shall be stopped manually with the switch on the instrument panel.

2.5.12   Fuel System

Fuel system consisting of storage tank, day tank, connecting piping, and accessories shall conform to the applicable items of NFPA 30 and NFPA 37.  A horizontal aboveground storage tank with a capacity of 1000 liters shall be provided for the storage of No. 2 diesel fuel. The storage tank shall be constructed, installed, and tested as specified in relevant Section FUEL STORAGE SYSTEMS.

2.6   	EQUIPMENT APPURTENANCES

2.6.1   Attachments

All necessary bolts, nuts, washers, bolt sleeves, and other types of attachments for the installation of the equipment shall be furnished with the equipment. Bolts shall conform to the requirements of ASTM A 307 and nuts shall be hexagonal of the same quality as the bolts used.  Threads shall be clean-cut and shall conform to ASME B1.1. Bolts, nuts, and washers specified to be galvanized or not otherwise indicated or specified, shall be zinc coated after being threaded, by the hot-dip process conforming to ASTM A 123/A 123M as appropriate. Bolts, nuts, and washers specified or indicated to be stainless steel shall be Type 316.

2.6.2   	Equipment Guards

Equipment driven by open shafts, belts, chains, or gears shall be provided with all-metal guards enclosing the drive mechanism. Guard shall be constructed of galvanized sheet steel or galvanized woven wire or expanded metal set in a frame of galvanized steel members. Guards shall be secured in position by steel braces or straps, which will permit easy removal for servicing the equipment.  The guards shall conform in all respects to all applicable safety codes and regulations.

2.6.3   	Tools

A complete set of all special tools, which may be necessary for the adjustment, operation, maintenance, and disassembly of all equipment shall be furnished.  Special tools are considered to be those tools which because of their limited use are not normally available, but which are necessary for the particular equipment.  Special tools shall be high-grade, smooth, forged, alloy, tool steel. One pressure grease gun for each type of grease required for motors and diesel engines shall also be furnished. All tools shall be delivered at the same time as the equipment to which they pertain. The Contractor shall properly store and safeguard such tools until completion of the work, at which time they shall be delivered to the Engineer.

2.6.4   	Shop Painting

All motors, pump casings, and similar parts of equipment customarily finished in the shop shall be thoroughly cleaned, primed, and given two finish coats of paint at the factory in accordance with the recommendations of the manufacturer.  Ferrous surfaces not to be painted shall be given a shop coat of grease or other suitable rust-resistant coating.

PART 3 EXECUTIONS

3.1   	INSTALLATION

Each pump and engine shall be installed in accordance with the written instructions of the manufacturer and under the direct supervision of the manufacturer's representative.  Engine fuel supply system shall be installed as indicated and in conformance with NFPA 30 and NFPA 37.

3.1.1   Concrete Foundations

Concrete for equipment foundations and for any required ballast for fuel storage tanks shall be as specified in relevant Sections. Concrete foundations shall be integral with and of the same class as that of the building floor unless otherwise indicated. Concrete having a compressive strength of at least 17 MPa shall be used in foundations that are entirely separated from the surrounding floor. A premolded filler strip shall be installed between the foundation and floor slab as shown. Foundation bolts, as required, shall be furnished for proper positioning during the placement of the concrete.

3.2   	TESTS

After installation of the pumping units and appurtenances is complete, operating tests shall be carried out to assure that the pumping installation operates properly. The Contractor shall make arrangements to have the manufacturer's representatives present when field equipment tests are made.  Field tests for fire service pumps and engines shall conform to NFPA 20. Each pumping unit shall be given a running field test in the presence of the Engineer for a minimum of 2 hours with each combination of electric motor and engine drive. Each pumping unit shall be operated at its rated capacity or such other point on its head-capacity curve selected by the Engineer. The Contractor shall provide an accurate and acceptable method of measuring the discharge flow. Each engine shall be operated for a minimum of 4 hours at a point of maximum horsepower indicated on the pump head-capacity curve or such other point on the curve selected by the Engineer. Tests shall assure that the units and appurtenances have been installed correctly, that there is no objectionable heating, vibration, or noise from any parts, and that all manual and automatic controls function properly.  If any deficiencies are revealed during any tests, such deficiencies shall be corrected and the tests shall be reconducted.

3.3   	FIELD PAINTING

Stainless steel, galvanized steel, and nonferrous surfaces shall not be painted.

3.3.1   Touch-Up Painting

Factory painted items requiring touching up in the field shall be thoroughly cleaned of all foreign material and shall be primed and top coated with the manufacturer's standard factory finish.

3.3.2   	Exposed Ferrous Surfaces

Exposed ferrous surfaces shall be painted with two coats of enamel paint conforming to SSPC Paint 21. Factory primed surfaces shall be solvent-cleaned before painting. Surfaces that have not been factory primed shall be prepared and primed with one coat of SSPC Paint 25or in accordance with the enamel paint manufacturer's recommendations.

3.4   	MANUFACTURER'S REPRESENTATIVE

The Contractor shall obtain the services of a manufacturer's representative experienced in the installation, adjustment, and operation of the equipment specified. The representative shall supervise the installation, adjustment, and testing of the equipment.  Up to 30 days service shall be provided at no expense to the Owner.

3.5   	DEMONSTRATION

Upon completion of the work and at a time designated by the Engineer, the services of one or more competent engineers shall be provided by the Contractor for a training period of not less than 80 hours to instruct a representative of the Owner in the operation and maintenance of equipment furnished under this section of the specifications. These field instructions shall cover all the items contained in the bound instructions.

End Of Section

SECTION:  10.00

MEDICAL GAS AND VACUUM PIPING

## PART 1   GENERAL

This section covers requirements for Medical Gases and Vacuum Systems. It includes, medical gases piping, medical air compressors and receivers, vacuum pumps and receivers, manifold gases for Oxygen, Nitrous Oxide and related accessories.

1.1   	SUBMITTALS

Submit the following in accordance with relevant section for Submittal Procedures.

Shop Drawings

Medical gas systems

Vacuum systems

Equipment foundations

Product Data

Compressors

Manifolds

Station outlets and terminal units

Pipe and fittings

Pumps

Specialties

Valves

Vibration isolators

Test Reports

Component tests

Cross-connection tests

Final alarm tests

Final purging and testing

Gas source tests

Holding charges

Medical air compressor and vacuum pump tests

Positive pressure tests

System contaminant level tests

Vacuum systems tests

The testing agency shall prepare test reports for systems, equipment, and station outlets and terminals. The testing agency may either mobilize on the project site or test gas samples from sample bottles submitted by the Contractor. Upon completion of field tests, the Contractor shall provide documentation of the name of individuals performing tests and actual testing procedures. The Contractor shall provide a certification that test results were within limits permitted by these specifications.

Certificates

Detail field testing procedures

Medical gas systems testing agency qualifications

Welder and brazer procedures and qualifications

Operation and Maintenance Data

Compressors

Medical gas cylinder manifold systems

Medical air systems

Pumps

Closeout Submittals

Compressors

Medical air systems

Medical gas cylinder manifold systems

Piping systems diagrams

Pumps

1.2   	QUALITY ASSURANCE

Materials, performance, installation, and testing shall comply with NFPA 99 and HTM 2022, with modifications and additions specified herein. The NFPA 99 and HTM 2022 recommendations shall be considered as mandatory requirements. Substitute the word "shall" for the word "should" in these manuals.

1.2.1   	Procedures and Qualifications

Submit detail field testing procedures, medical gas systems testing agency qualifications, and welder and brazer procedures and qualifications.  Include data on test methods, testing instruments and equipment, and instrument calibration sources and method references.

1.2.2   	Qualifications of Testing Agency

Provide a testing agency for the approval of the Engineer. The testing agency shall be independent of the medical gas equipment manufacturer and contractor.  Provide names and locations of three projects where testing of gas systems has been performed by the testing agency. Include names and phones of owners and project supervisors for these projects. Provide a written statement that these projects are of similar scope of that stipulated in this specification.

1.2.3   	Welder and Brazer Procedures and Performance Qualifications

Comply with AWS B2.1 and AWS B2.2.

1.2.4   	Regulatory Requirements

AWS Z49.1 for brazing, soldering, and welding; 29 CFR 1910.104 for oxygen; and CGA G-8.1 for nitrous oxide.

1.2.5   	Design Requirements

1.2.5.1   Detail Drawings

Submit A0 detail working drawings showing medical gas systems:  oxygen, nitrous oxide, and medical air; vacuum systems: vacuum, and anesthesia gas evacuation systems; and equipment foundations: noise and vibration isolators, equipment bases, inertia bases, and foundations for equipment and piping.

1.2.5.2   Piping Systems Diagrams

Submit texts and piping systems diagrams of oxygen, nitrous oxide, and medical air.

## PART 2   PRODUCTS

2.1   	MATERIALS

2.1.1   	Pipe and Fittings

Sized and made for pressures and other design conditions as indicated.

2.1.1.1   Metal Pipe and Fittings

Oxygen, Nitrous Oxide, Medical air, and Vacuum systems (include anesthesia gas evacuation system):

ASTM B 88M or ASTM B 280 ACR (air conditioning and refrigeration), seamless Type K or L hard-drawn copper tubing for above ground and inside buildings, and soft drawn (annealed) for underground.  Provide ANSI B16.18 cast copper, ASME B16.22 wrought copper, fittings.

2.1.2   Valves

NFPA 99, sized and made for pressures and other design conditions as indicated.  Valves of same type shall be the product of one manufacturer, uniform in pattern and appearance, color coded and labeled for the intended service.  Identification plates may be used in lieu of labels. Submit calibration chart of the flow measuring device of each pressure reducing regulator.

2.1.2.1   Ball Valves (Oxygen and Nitrous Oxide)

For sizes 50mm or smaller, MSS SP-110, copper alloy valve design which permits inspection and repair of seats and seals without removing the valve body, or valve ends, from the line. For sizes 65mm or greater, MSS SP-72, flanged connections, bronze or stainless steel body. Provide double-seal construction with replaceable Buna-N, neoprene, or polytetrafluoroethylene (TFE) seat seals.  Provide valves suitable for at least 2068 kPa (gage), cold water, non-shock working pressure.

2.1.2.2   Diaphragm Valves (Oxygen and Nitrous Oxide)

MSS SP-88, brass-bodied, packless, diaphragm type with regrindable or renewable seats and disks capable of being disassembled in line for servicing o-ring and seating surfaces.  Provide valves suitable for at least 2068 kPa (gage), cold water, non-shock working pressure.

2.1.2.3 Pressure Reducing Regulators

Hospital regulators with a calibrated flow measuring device and CGA V-1valve connections. Minimum accuracy of flow measure device shall be plus or minus 3 percent for the intended use.

2.1.2.4 Gate Valves (Vacuum, Medical Air, and Anesthesia Gas Evacuation)

MSS SP-80 bronze, solder ends.

2.1.3   	Specialties

2.1.3.1 Hangers and Supports

Steel adjustable type per MSS SP-58 and MSS SP-69. Provide hangers, supports, nuts, bolts, and washers with hot-dip galvanized finish after fabrication.

2.1.3.2 Piping Isolators

Commercial metal clad hair felt type for isolating pipe from hangers.

2.1.3.3 Pressure Gages

ASME B40.1 with restrictor, except that gages for oxygen and nitrous oxide systems shall be manufactured and labeled expressly for the intended service, and marked "DO NOT USE OIL." Provide gages with white dials and black lettering, and with sizes, ranges, and case type, as indicated.

2.1.3.4 Vacuum Bottle Brackets

Stainless steel with finish matching adjacent station outlet.

2.1.3.5 Flexible Connectors

Manufactured expressly for operating conditions annular and helically corrugated flexible, single ply, seamless or seam-welded tubing with one or more layers of stainless steel or bronze wire braid, or reinforced TFE bellows or hose. Use manufacturer's recommended lengths and sizes for the intended service.

2.1.3.6 Sleeves

Provide plastic waterproof cement seal or mechanically adjustable segmented elastomeric seal.  In Concrete and Masonry, use galvanized steel pipe, ductile-iron, or cast-iron.  For partitions, floors and roofs, other than concrete or masonry, use 26-gage galvanized sheet steel.

2.1.3.7 Brazing Alloy

AWS A5.8, BCuP (Brazing-Copper-Phosphorus) series, greater than 538 degrees C melting temperature.  Use only cadmium free brazing filler.  Do not use flux for copper-to-copper connections.

2.1.3.8 Soldering Alloys

ASTM B 32, Alloy Grade Sb5, Sn94, Sn95, or Sn96.

2.1.3.9 Welding Filler Metal

AWS A5.28 and compatible with the materials.

2.1.3.10 Threaded Joint Tape

TFE.

2.1.3.11   Area Service Valve Cabinets

Stainless steel, flush-mounted, commercially available items with welded joints, and rigidly assembled. Provide boxes of proper size to accommodate valve and fittings. Punch or drill sides to receive tubing.  Provide anchors to secure cabinets to wall construction.

a.  	Cover Plates: Stainless steel. Provide covers with replaceable plastic windows with a corrosion resistant device or lever, secured to cover for removal of window in an emergency.

b.  	Cabinet Labels: Each valve or valve cabinet shall be labeled for substance and color coded as follows: "CAUTION (intended service) TO (area served)." Color coding shall be the same as for the adjoining pipe.

2.1.3.12 Buried Piping

Encase in protective Schedule 40 PVC pipe. For oxygen piping, provide Factory Mutual (FM) listed heat trace, set for 27 degrees C maximum, terminated at a junction box with terminal board, and mounted near the main oxygen supply shut-off valve just inside the building. Label the junction box "Underground Oxygen Piping Heat Trace." Do not permanently wire heat trace to electrical power. Provide buried lines with 25 mm ASTM C 552 cellular glass and integral moisture barriers.

2.1.3.13 Buried Pipe Warning and Identification Tape

Provide detectable aluminum foil plastic backed tape or detectable magnetic plastic tape manufactured for warning and identification of buried piping. Tape shall be detectable by an electronic detection instrument. Provide tape in rolls, 80mm minimum width, color coded for the service involved with warning and identification imprinted in bold black letters continuously and repeatedly over entire tape length.  Use "CAUTION (intended service) LINE BURIED BELOW" or similar wording.  Use permanent code and letter coloring unaffected by moisture and other substances contained in trench backfill material.

2.1.3.14 Piping Identification

FS A-A-1689, pressure sensitive adhesive tape and decals. Colors and labels must conform to ANSI A13.1.

2.1.3.15 Equipment Foundations

Refer to relevant section Mechanical Sound, and Vibration Control," and as recommended by the equipment manufacturer.

2.1.4   	Station Outlets and Vacuum Terminals (Inlets)

Sized and made for pressures and other design conditions, as indicated.

2.1.4.1   Connectors

Permanently label and color code female connectors and include the warning "DO NOT USE OIL." Permanently label and color code male connectors.  Provide labels with cast-in or engraved letters.

a.  	Diameter-Index Safety System (DISS) Connectors: CGA V-5 brass connections with color code, automatic valve, & secondary check valve. Provide each outlet connector with a positive acting metal or plastic cap secured with chain to the faceplate.

b.  	Commercial Connectors: Quick coupler with non-interchangeable code key on fitting with color code, automatic valve, and secondary check valve.

2.1.4.2   Ceiling Hoses

Provide conductive neoprene hoses with color code for appropriate service. Provide sufficient hose length capable of dropping to within 1.50 meters from the floor. Provide chrome-plated, spring loaded, hose retractor kits to automatically withdraw hose assembly for a minimum of 508mm retraction from the fully extended position of the hoses. For the upper end of hoses, use female DISS connectors with nuts. For the lower end of hoses, use commercial connectors.

2.1.4.3   Color Code and DISS Number Requirements

TABLE 1

COLOR CODED CONNECTORS WITH DISS NUMBER

Gas              Color        DISS          Automatic      Secondary

Code         Number        Valve          Check Valve

___              _____        ______        _________      ____________

Oxygen         Green        1240          Yes            Yes

Nitrous          Blue          1040          Yes            Yes

Oxide

Medical Air    Yellow       1160          Yes            Yes

Vacuum         White       1220          Yes            Optional

Anesthesia       Purple       2220          Yes            No

Gas Evacuation

2.1.4.4   Station Outlets and Terminal Units

Provide DISS non-interchangeable connectors, automatic valves, secondary regulating and check valves (except evacuation outlets and vacuum terminals), and capped 10mm tubing stubs for supply connections color coded and labeled for the intended services. Rigidly secure outlets in outlet boxes. Permanently label outlets and terminals with engraved faceplates or engraved laminated plastic plates color coded for the intended service.

a.  	Wall Type: Flush mount in galvanized steel or cast aluminum boxes with stainless steel faceplates.

b.  	Fixed Column Ceiling Type: Mount on fixed columns fabricated of stainless steel with removable access panels and attachment provisions for adjustable auxiliary equipment hooks and slides.

c.  	Flush-Mounted Ceiling Type: Mount in galvanized steel or cast aluminum boxes with stainless steel or chrome-plated brass faceplates. Provide hose drops to a height of 2 meters above floor. Provide color coded conductive hoses with connectors at top and bottom. In accordance with Table 1, provide valves at the hose outlet connector.

2.2   	EQUIPMENT

2.2.1   Alarms

Provide enameled steel of minimum 16 gage, NEMA ICS 6, modular, master alarm panel for each appropriate medical and vacuum systems.  Provide service indicator lights and alarm signal testers.  Provide alarm signal testers with test buttons or switches to temporarily activate visual signals and audible signals to test the system status.

2.2.1.1  "Reserve In-Use" Switchover Alarm

For medical gas cylinder manifold systems, provide alarm, which activates when any reserve medical gas supply goes into operation.

2.2.1.2 Pressure Alarms

For failure alarms for medical air compressors and vacuum pumps, provide low and high pressure switches, of either contact or mercury (Hg) type, to activate alarms when pressure either drops or rises. Set operating pressure differentials at 21 kPa (gage) minimum.

2.2.1.3 Dew Point Alarm (Medical Air System)

Provide local non-cancelable visual and cancellable audible alarm.  This alarm is activated by receiving signal from the dew point monitor, when the pressure dew point rises above 6 degrees C at 690 kPa (gage).

2.2.1.4 Air Filter Alarm (Medical Air Systems)

Provide differential pressure switch for the filter to activate an alarm when pressure drop across the filter exceeds 14 kPa over that when the filter is new and clean.

2.2.1.5 High Temperature Shutdown Alarm (Medical Air Systems)

Provide temperature switch to activate an alarm and shutoff the compressor when the discharge-air temperature exceeds 177 degrees C.

2.2.1.6 High Carbon Monoxide Level Alarm (Medical Air Systems)

For compressor with carbon monoxide monitor only, provide local non-cancellable visual and cancellable audible alarm to alarm when carbon monoxide levels rises above 15 milligram per kilogram.

2.2.1.7 Oil Filter Alarm (Vacuum Pumps)

Provide differential pressure switch for the discharge-oil filter to activate an alarm upon sensing backpressure or rising pressure drop beyond a set level.

2.2.1.8 Low Vacuum Alarm (Vacuum Pumps)

Provide vacuum switch to activate an alarm when the system vacuum upstream of shutoff valve drops below 41 kPa.

2.2.2   	Medical Gas Cylinder Manifold Systems

Provide non-ferrous manifold, fittings, valves, parts, and connections rated at 20,682 kPa (gage) working pressure for each type of medical gas as indicated.  Non-ferrous materials include aluminum, brass, bronze, monel, and inconel.

2.2.2.1 Cylinder Banks

Duplex manifold arrangement with cylinder connections per bank as indicated on drawings. Provide each bank with a two-stage pressure regulator with built-in safety valves and pressure gages, check valves, cylinder connecting coils and handles, header valves, and all other required equipment. Pressure regulator shall reduce 20,682 kPa (gage) cylinder pressure to 690 kPa (gage) for system delivery.

2.2.2.2 Bank Switch-Over

Only one cylinder bank shall be used at one time. Switch-over from exhausted to full cylinders shall be automatic and without pressure fluctuation. Provide a pressure regulating valve down stream of switch-over valves. Resetting of manifold controls shall be automatic or manual after the replacement of empty cylinders. Pressure switch shall actuate switch-over controls and "Reserve In-Use" alarms. House manifold controls in a sheet steel cabinet.

2.2.3   	Medical Air Systems

Provide medical compressed air with minimum air quality of ISO 8573-1, Class 1.3.1.

2.2.3.1   Air Compressors

Submit manufacturer, model, operating speed (revolutions per second), capacity (liter per second (L/s), free air delivered at indicated pressure), bearings, lubrication, receiver capacity (liter), electric motor (manufacture, frame, type, speed, current characteristics, and kilowatt), thermal cutoff switch (manufacturer, type, & model), starter (manufacturer, type, & model), air silencer (manufacturer, type, & model), air filter (manufacturer, type, & model), air cooler (manufacturer, type & model), & air dryer (manufacturer, type, and model. Oil-free piston compressors with steel body construction, capable of continuous operation at indicated discharge pressures and compatible with pneumatic surgical or medical hand pieces. Provide filter-muffler intake for each compressor.  Provide outlet filters.

2.2.3.2   After coolers

Steel body construction. Size after coolers for cooling the air to within 15 degrees of inlet water temperatures. Provide solenoid or automatic valve to shut off cooling water when compressor is not running.

2.2.3.3   Drives

Provide direct drives with flexible couplings or V-belt drives.

2.2.3.4 Receivers

Welded steel tanks with BS 5169-1992 Class-III code and certified for pressure rating. Protect interior and exterior surfaces of receivers with a factory-applied 0.13mm minimum non-toxic enamel or galvanized coating. Provide necessary gages, switches, and automatic drains as recommended by manufacturer.

2.2.3.5 Medical Air Dryers

Self contained, refrigerated, hermetic compressors, moisture separator, heat exchanger, automatic controls, and automatic drains. At 38 degrees C ambient, provide minimum drying capacity to produce a constant-3 degrees C dew point medical air.  Provide an enameled steel housing. Provide cycling or non-cycling controls in accordance with manufacturer's recommendation. Provide dew point monitor with digital or gage display, carbon monoxide monitor with high carbon monoxide level alarm, and interface with the master alarm panels.

2.2.3.6   Intake Air Filter and Muffler

Dry-inlet filter and muffler with silencer tubes. Provide replaceable one micron filter elements.

2.2.3.7   Outlet Air Filters

Provide one micron filters of the indicated liter per second capacity and working pressure.

2.2.3.8   Failure Alarms

Provide pressure switch to activate audible and visual alarms when compressed air pressure falls below 20 percent of the predetermined setting. Provide high water level shutdown or alarm switches for the receivers.

2.2.3.9   Automatic Controls

Provide automatic controls for alternating the units on start-up and to prevent simultaneous start-up of two or more units when on emergency power.

2.2.4   	Vacuum Pumps

Submit manufacturer, model, operating speed, capacity (liter per second, free air exhausted from rated vacuum), bearing, lubrication, adjustment of drive, capacity of tank (liter), electric motor (manufacturer, frame, type, speed, current characteristics, and kilowatt), thermal cutout switch (manufacturer, type, and model), and motor starter (manufacturer, type, and model). Provide rotary or centrifugal pumps with stainless steel body construction. Provide pumps capable of continuous operation at indicated vacuum.

2.2.4.1   Outlet Mufflers and Vents

Provide pumps with outlet mufflers.

2.2.4.2 Drives

Electric motor driven with either flexible couplings or V-belt drives.

2.2.4.3 Vacuum Receivers

Welded steel tanks with BS 5169-1992 Class III code and certified for the indicated vacuum pressures. Protect interior and exterior surfaces of receivers with factory-applied 0.13mm minimum non-toxic enamel or galvanized coating. Provide necessary gages, switches, and drains as recommended by the manufacturer.

2.2.4.4   Failure Alarms

Provide pressure switch to activate alarm when vacuum pressure falls 20 percent below predetermined setting.

2.2.4.5 Automatic Controls

Provide automatic controls for alternating the units on startup and prevent simultaneous start-up of two or more units when on emergency power.

2.2.4.6 Solenoid Valves

For vacuum pumps of the water seal or water displacement construction, provide brass, bronze, or steel body.  Provide solenoid valve to cut off water supply when the pump is not running.

2.2.5   	Anesthesia Gas Scavenging Pumps

Provide water-seal, positive-displacement, non-pulsating, vacuum pumps for handling flammable gases. Provide capability of a maximum vacuum level of 85 kPa. Ensure pump numbers, sizes, capacities, and operating pressures (vacuum) are as indicated.

2.2.5.1   Heat Exchanger

Provide minimum 90 percent water recirculation system with heat exchanger and controls.  Provide a solenoid valve in the pump water supply to shut off the water when the pump is not running.

2.2.5.2   Motor Controls

Provide automatic, adjustable, vacuum-sensing, hand-off-automatic, electric switch; NEMA ICS 6, Type 12, UL Listed, dustproof control panel; circuit breakers for each control circuit; hour meter; magnetic starter; and heavy-duty alternator for the motors.

## PART 3 EXECUTIONS

3.1   	INSTALLATION

Comply with NFPA 50, NFPA 99, and HTM 2022. Provide vibration isolation and noise isolation and equipment in accordance with relevant Section for "Mechanical Sound, and Vibration Control."

3.1.1   	Piping

3.1.1.1   Pre-Installation Cleaning

Disassemble positive pressure pipe, fittings, valves, and other components. Provide only pipe and fittings, which have been thoroughly washed.  Use the following cleaning procedures:

a.  	Mix the solution of sodium carbonate or trisodium phosphate in the proportion of 454 gram dry chemical in 11.40 liters of water.

b.  	Maintain the resulting solution at minimum 82 degrees C.

c.  	Wash thoroughly, scrubbing as required. Rinse with clean water and blow dry with oil-free dry nitrogen.

Effectively cap ends of the pipe, fittings or valves, and label "CAUTION! CLEANED FOR MEDICAL GAS SERVICE." In lieu of cleaning by the installer at the job site, each pipe, fitting and valve may be supplied "CLEAN FOR OXYGEN SERVICE" by the manufacturer. Do not use carbon tetrachloride, hydrocarbon, or halogenated hydrocarbon solvents.

3.1.1.2   Piping Installation

Exercise care with cutting, brushing, and reaming tools and equipment to prevent oil, grease, and dirt from entering pipe and components.  Rewash contaminated pipe and components. Cut pipe square and accurately to measurements and work into place without springing or forcing.  Follow the general arrangement indicated. At the end of each work shift shut off valves, and cap or plug open ends. As work progresses, valve off each section to prevent moisture or dirt from entering piping.

3.1.1.3   Hangers and Supports Installation

Install hangers and supports in accordance with MSS SP-69 and MSS SP-89 except that spacing of the hangers and supports shall be in accordance with Table 2.

TABLE 2

MAXIMUM SPAN FOR PIPE HANGERS (mm)

Copper tube, Type K (Cu-K) and Type L (Cu-L)

Pipe Size     Cu-K                Cu-L

(mm)

10           1060               800

15           1140               1060

20           1290               1290

25           1520               1440

40           1750               1670

50           1980               1980

65           2210               2130

80           2360               2280

3.1.1.4 Exposed Oxygen Piping

Install in wall-mounted sheet steel raceways and junction boxes.

3.1.1.5 Threaded Joints

Coat male threads of fittings used in shut off valves with TFE tape before assembly.

3.1.1.6 Brazing and Soldering

Personnel qualification procedures shall conform with AWS B2.2. Metal preparation and joining procedures shall conform with CDA Tube Handbook and NFPA 99. Use BCuP Series brazing alloys for joints, except for 50mm and smaller pipes, in vacuum systems only, solder joints may be used. Completely clean off excess after brazing and soldering.

3.1.1.7 Welding

Comply with AWS B2.1.

3.1.1.8 Cleaning of All Piping

During brazing, soldering, or welding operations, continuously purge with oil-free dry nitrogen. As each section is completed, blow lines clear of dirt and contamination with oil-free dry nitrogen in accordance with NFPA 99.  Cap or plug open ends, when left unattended

3.1.1.9 Pitch

Pitch piping in the direction of flow.  Do not trap except where indicated.

3.1.1.10 Changes in Size

Effect changes in size with reducing fittings.  Do not use bushings.

3.1.1.11 Pipe Sleeves

Provide where pipes and tubing pass through walls, floors, roofs, and partitions. Leave 6mm clearance around pipes. Secure sleeves in proper position and location before and during construction. Ensure sleeves of sufficient length to pass through entire thickness of walls, partitions, or slabs. Cut sleeves flush at both ends except that sleeves in floor slabs shall extend 50mm above the finished floor. Firmly pack space between pipe or tubing and sleeve with mineral wool insulation. Seal space at both ends of sleeve or core-drilled hole with plastic waterproof cement, which will dry to a firm but pliable mass. In lieu of plastic cement seal, a mechanically adjustable segmented elastomeric seal may be used.

3.1.1.12   Identification of Piping

Identify piping in accordance with ANSI A13.1, except provide tape and decals conforming with FS A-A-1689 in lieu of stencils and paint. Provide copies of the piping identification code and piping layout schematic framed under glass and install where required.

3.1.2  	Valves

Disassemble solder socket end valves before brazing, soldering, or welding to prevent damage to seats and seals. Except in flush wall mounted cabinets, install valves with stem vertical and with valves accessible for operation and maintenance. Install strainers on the inlet side of pressure reducing valves.  Provide main gas valves, pressure reducing or flow control, with by-passes and isolation valves, to permit main valve maintenance and permit flow to patient care areas without interruption of gas.

3.1.2.1   Purge Vent Valves

Provide purge vent valves at the bottom of vertical risers 3 meters or more in height. Up stream of the building entrance, also provide shut-off valves for buried lines and lines of 40 mm and larger for above ground lines. Valves and connecting pipe shall be 25 mm or line size if smaller than 25mm. After completion of tests, seal vent valve outlets with brazed caps.

3.1.3   	Manifolds

Vent relief valves to the outside of the building.

3.1.4   	Alarms

Install alarm systems in accordance with NFPA 99 and HTM 2022.

3.1.5   	Equipment

3.1.5.1 Equipment Foundations

Provide equipment foundations of sufficient size, weight, and proper design to prevent shifting of equipment under operating conditions.

3.1.5.2 Equipment Installation

Install equipment in accordance with manufacturer's written instructions and as indicated. Grout equipment mounted on concrete foundations before piping is installed.

3.1.5.3 Receivers

Provide a valved bypass around receivers.

3.1.5.4 Medical Air Systems

Make tie-in point for the compressor for medical air piping systems at a flange or union joint, following completion and approval of air quality testing of the compressor.

3.1.6   	Electrical Work

Comply with NFPA 70 and relevant sections of electrical specifications. Ground metal piping systems. Provide electric motor driven equipment specified herein complete with motors, motor starters, and controls. Provide motor starters complete with thermal overload protection and other appurtenances necessary for the motor control specified. Provide manual or automatic control and protective devices required for the operation of equipment.

3.2   	FIELD QUALITY CONTROL

The Engineer will witness field tests. For field testing and validation by a third party testing agency, the Contractor shall provide a qualified testing agency as approved by the Engineer. The Contractor shall give the Engineer 14 days prior notice for dates and times for acceptance tests.

3.2.1   	Agency Testing

Tests for contaminants and system validations are required for medical gas systems.

3.2.2   	Sample Bottles

When gas sample bottles are to be used, the bottles are to be supplied by the testing agency, sealed and ready for use, and filled and labeled in accordance with the agency's written instructions.

3.2.3   	Test Instruments

Provide vacuum gages with 2 kPa increments, readable to one kPa. Provide pressure gages with 2 kPa (gage) increments, readable to one kPa (gage). Use only correct adapters for gages.  Do not use universal adapters.

3.2.4   	Pressure Test Gases

During initial purging, blowing out, and pressure testing, use only oil-free dry nitrogen conforming with CGA G-10.1, Grade F, except that hydrocarbons and halogenated hydrocarbons shall not exceed the limits in Table 4, "Test Gas Purity, Contaminate Levels, and Test Methods." Use no other gas, material, or liquid during purging and tests.

3.2.5  	Outlet Adapters

Use only correct adapters for specified medical gas outlets. Do not use universal adapters.

3.2.6   	Positive Pressure Tests

Test only one system at a time. Test each joint with soap solution, repair leaks found, and retest. In the systems not being tested, install pressure gages, bleed to zero pressure, and seal. Investigate the cause of significant pressure rise in the systems not being tested.

3.2.6.1   Leak Tests, Low Pressure Systems

Less than 4136 kPa (gage). Test each section of each system at 1034 to 1379 kPa (gage) with oil-free dry nitrogen. When design pressure is greater than 1379 kPa (gage), pressurize each section in 350 kPa (gage) increment until the design pressure is reached.

3.2.6.2   Equipment Pressure Tests

Test joints with the system at 1034 kPa (gage) with the equipment connected limited to the rough-in portion of service outlets. Do not connect equipment until after the test is completed. Carefully wipe off soapsuds and seal openings against contamination until tanks or equipment are connected.

3.2.6.3 Final Pressure Tests, Low Pressure Systems

Pressure test with nitrogen at 120 percent of design pressure for 24 hours. No pressure drop, except due to temperature change, will be accepted. Allow for ambient temperature change in accordance with the relationship PF+101.32=(P1+101.32) (T2+273) (T1+273), in which T and P represent Centigrade temperature and gage pressure respectively, numbers 1 and 2 denote initial and final readings respectively, and PF is the calculated final pressure. When PF exceeds the measured final pressure, retest each section individually, and apply soap solution to all joints of each section for which a reduction in pressure occurs after allowing for ambient temperature change. Repair leaking joints and repeat test until no reduction in pressure occurs. Use a test gage calibrated in 2 kPa increments and readable to one kPa (gage).

3.2.7   Vacuum Systems Tests

Test vacuum and anesthesia gas evacuation systems.

3.2.7.1   Leak Tests

After installation of outlet valves but before installing vacuum pumps and alarm switches, pressurize each section of each system with oil-free dry nitrogen to 414 kPa and test with soap solution.  Repair leaks and retest.

3.2.7.2 Final Pressure Tests

Pressurize system with oil-free dry nitrogen to 173 kPa (gage) for 24 hours. No pressure drop, except due to temperature change, will be accepted.  Allow for ambient temperature change in accordance with the relationship PF + 101.32 = (P1 + 101.32) (T2 + 273)/(T1 + 273), in which T and P represent Centigrade temperature and gage pressure respectively, numbers 1 and 2 denote initial and final readings respectively, and PF is the calculated final pressure. When PF exceeds the measured final pressure, retest each section individually, and apply a soap solution to all joints of each section in which a reduction in pressure occurs after allowing for ambient temperature change. Repair leaking joints and repeat test until no reduction in pressure occurs. Use a test gage calibrated in 2 kPa increments and readable to one kPa (gage).

3.2.7.3   Vacuum Tests

After the installation of alarm switches, evacuate each system to 54 kPa, or to the indicated kPa for oral evacuation system, and test each outlet's pressure (vacuum) with a test gage calibrated in 2 kPa increments and readable to one kPa.

3.2.7.4 Cleaning

Carefully wipe off soapsuds and seal openings against contamination until tanks or equipment are connected.

3.2.8   	Cross-Connection Tests by Testing Agency

Comply with NFPA 99. Pressurize each system with nitrogen in accordance with Table 3. Check 100 percent of the outlets in each system. Include anesthesia gas evacuation in vacuum systems.

TABLE 3

CROSS-CONNECTION TEST PRESSURES

System      	Primary System kPa (gage) 	Secondary System kPa (gage)

Vacuum                	   --   	                           	  69

Nitrous Oxide         	  690     	                        276

Oxygen                	  862                 	            345

Medical Air           	1035                            	414

3.2.9   	Medical Air Compressor and Vacuum Pump Tests by Testing Agency

Operationally test each unit through their respective pressure and capacity ranges. Test control operations from start-up, low through high speeds, shut-down and emergency functions and safety limits. Check each unit for conformance with the indicated or specified performance requirements. Test medical air from compressor dryer/filter systems for contaminants in accordance with paragraph entitled "Medical Air Purity, Contaminate Levels, and Test Methods."

3.2.10   Component Tests by Testing Agency

Test system controls, alarms, pressure switches, and equipment operations.  Verify the flow rate accuracy of each pressure reducing regulator.

3.2.11   Final Purging and Testing by Testing Agency

Use 414 to 448 kPa (gage), oil-free dry nitrogen to purge and clean medical air, oxygen, nitrogen, and nitrous oxide system 24 hours continuously for a minimum of 24 hours. Allow purge nitrogen to impinge upon a white cloth at a minimum flow rate of 100 liters per minute, until no evidence of discoloration is present and test gas used during the previous gas test has been removed from the piping systems. Bleed source gas for a minimum of one minute continuously through each terminal copper piping installed, as specified. After completion of purging and cleaning, completely remove temporary piping, adaptors, and connectors.

3.2.12   System Contaminant Level Tests by Testing Agency

3.2.12.1 Test Gases

After final purging and cleaning, test for contamination in medical air, oxygen, and nitrous oxide systems. For medical air system tests, use medical air as test gas Minimum flow rate of test gas shall be 100 liters per minute.

3.2.12.2 Test Gas Purity, Contaminate Levels, and Test Methods

Table 4 lists limits of contaminants or concentration minimums in the test gases used for purging and testing in oxygen, and nitrous oxide systems, and test methods to be used to determine levels of contaminants and concentration minimums.

a.  	Test Gas:99 percent by volume minimum; gas chromatography or equivalent

b.  	Solid Particulate: 2 milligrams per cubic meter maximum; 0.8 micron pore size filter.

c.  	Hydrocarbon Compounds: One part per million, concentration volume per volume, maximum expressed as methane equivalents; gas chromatography or equivalent.

d.  	Halogenated Hydrocarbon Compounds: 2 parts per million, concentration volume per volume, maximum; mass spectrometry, infrared spectrometry, or gas chromatography.

e.  	Carbon Monoxide: 2 parts per million, concentration volume per volume, maximum; gas chromatography, electrochemical carbon monoxide analyzer, or equivalent.

f.  	Water (Moisture): Minus 50 degrees C dew point; Pittsburg cup, dew point hygrometer, or electronic hygrometer.

3.2.12.3 Medical Air Purity, Contaminate Levels, and Test Methods

Determine medical air purity and contaminate levels by testing air quality at the compressor, but before air is allowed to enter piping system. Test air samples from each medical air system including air intake areas, filter/dryer equipment outlets, and specified system outlets. Limit solid particulate levels below the specified filter efficiency levels. Limit moisture levels below that of the specified dryer outlet dew point. Use test methods specified HTM 2022 and NFPA 99

3.2.12.4 Contamination Tests

Test gas sources, equipment outlets, and system outlets using test methods specified in HTM 2022 and NFPA 99

3.2.12.5 Gas Source Tests

Test gas and air sources for contamination and gas concentrations. Purge oxygen, medical gas, and nitrous oxide systems with an appropriate gas until gases reach specified concentrations, clean and free of contamination.  Care must be taken to vent purged nitrous oxide and oxygen to the outside of the building and away from flames.

3.2.12.6 100 Percent Testing

Test 100 percent of the medical gas outlets in rooms, which are supplied with nitrous oxide.

3.2.12.7 10 Percent Testing

Test 10 percent of the medical gas outlets in areas, which are supplied only with oxygen or medical air.  Test such outlets to ensure the gas traversed the greatest length of pipeline.

3.2.12.8 Contaminated Systems

Clean and retest contaminated sections with one or more contaminated outlets. In rooms or areas where only oxygen or medical air is supplied, retest 20 percent of the outlets including the original 10 percent first tested. Each time contamination is found, repeat cleaning operation and increase number of outlets tested by 10 percent until zero percent contamination is obtained. Take care to vent purged nitrous oxide and oxygen to outside of building, away from flames.

3.2.13   Holding Charges by Testing Agency

After successful completion of contamination and gas concentration tests, pressurize each system to the operating pressure with the appropriate gas, shutoff valves, and cap outlets to keep systems free of contamination.

3.2.14   Final Alarm Tests by Testing Agency

Test and operate switches, alarms, and controls in each system with appropriate medical gases.

End Of Section

SECTION:  11.00

###### EQUIPMENT

Part 1 GENERAL

  - SUMMARY

        - This Section includes split-system air-conditioning and heat pump units consisting of separate evaporator-fan and compressor-condenser components. Units are designed for exposed or concealed mounting, and may be connected to ducts.

  - SUBMITTALS

        - Product Data:  Include rated capacities, furnished specialties, and accessories for each type of product indicated.  Include performance data in terms of capacities, outlet velocities, static pressures, sound power characteristics, motor requirements, and electrical characteristic s.

        - Shop Drawings:  Diagram power, signal, and control wiring.

        - Samples for Initial Selection:  For units with factory-applied color finishes.

        - Field quality-control test reports.

        - Operation and Maintenance Data: For split-system air-conditioning units to include in emergency, operation, and maintenance manuals.

        - Warranty:  Special warranty specified in this Section.

  - QUALITY ASSURANCE

        - Product Options:  Drawings indicate size, profiles, and dimensional requirements of split-system units and are based on the specific system indicated.  Refer to Division 1 Section "Product Requirements."

        - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

        - Energy-Efficiency Ratio:  Equal to or greater than prescribed by ASHRAE 90.1, "Energy Efficient Design of New Buildings except Low-Rise Residential Buildings."

        - Coefficient of Performance:  Equal to or greater than prescribed by ASHRAE 90.1, "Energy Efficient Design of New Buildings except Low-Rise Residential Buildings."

- Units shall be designed to operate with HCFC-free refrigerants

  - COORDINATION

        - Coordinate size and location of concrete bases for units.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork are specified in Division 3 Section "Cast-in-Place Concrete."

        - Coordinate size, location, and connection details with roof curbs, equipment supports, and roof penetrations specified in Division 7 Section "Roof Accessories."

  - WARRANTY

        - Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of split-system air-conditioning units that fail in materials or workmanship within specified warranty period.

- Warranty Period:  One year from date of Substantial Completion.

  - EXTRA MATERIALS

        - Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

- Filters:  One set of filters for each unit.

- HEPA FILTER

Supply and install duct line HEPA filter  efficiency 99.997 for  Ducting in

Operation, NICU,

Icu rooms including all accessories and fittings.

- Part 2      PRODUCTS

- 2.1 MANUFACTURERS

- Available Manufacturers:  Subject to compliance with requirements, manufacturers    offering products that may be incorporated into the Work include, but are not limited to, the following:

          - Carrier Air Conditioning; Div. of Carrier Corporation.

          - Lennox Industries Inc.

          - Mitsubishi Electric Sales Canada, Inc.

          - Sanyo Fisher (U.S.A.) Corp.

          - Trane Company (The); Unitary Products Group.

          - York International Corp.

          - Petra (Jordan).

- 2.2 WALL-MOUNTING/CEILING MOUNTING, EVAPORATOR-FAN     COMPONENTS

        - Cabinet:  Enameled steel with removable panels on front and ends in color selected by The Engineer, and discharge drain pans with drain connection.

        - Refrigerant Coil:  Copper tube, with mechanically bonded aluminum fins, complying with ARI 210/240, and with thermal-expansion valve.

        - Electric Coil:  Helical, nickel-chrome, resistance-wire heating elements with refractory ceramic support bushings; automatic-reset thermal cutout; built-in magnetic contactors; manual-reset thermal cutout; airflow proving device; and one-time fuses in terminal box for overcurrent protection.

        - Fan:  Direct drive, centrifugal fan.

        - Fan Motors:  Comply with requirements in Division 15 Section "Motors."

          - Special Motor Features:  Multitapped, multispeed with internal thermal protection and permanent lubrication.

        - Filters:  Permanent, cleanable.

- 2.3 DUCTED:

More than 50 Pa external static pressure.

Microprocessor temperature control.

Radial fan, vibration-free and quiet running. Protected by a thermal contact.

Sound pressure not more than 48 dBA @ high speed

- 2.4 CASSETTE:

Elegant, ceiling-mounted, white, impact-resistant, washable decoration panel.

Air suction through the panel below, which has an integrated, long-life air filter.

The air is discharged via four outlets with motorized, air vanes, which can be

vertically adjusted.

Two sides can be closed off to facilitate corner installation.

Turbo fan, phase controlled multiple steps, vibration-free and quiet running.

Protected by a thermal contact.

Fresh-air admixing can be admixed via a punched aperture.

Microprocessor temperature control.

Height not more than 300 mm.

Fan motor thermal protection.

Standard drain pump up to 800 mm.

Sound pressure not more than 48 dBA @ high speed.

- 2.5  AIR-COOLED, COMPRESSOR-CONDENSER COMPONENTS

- Casing:  Steel, finished with baked enamel in color selected by The Engineer, with removable panels for access to controls, weep holes for water drainage, and mounting holes in base.  Provide brass service valves, fittings, and gage ports on exterior of casing.

- Compressor:  Hermetically sealed with crankcase heater and mounted on vibration

- isolation.  Compressor motor shall have thermal- and current-sensitive overload devices, start capacitor, relay, and contactor.

- Compressor Type:  Reciprocating.

- Two-speed compressor motor with manual-reset high-pressure switch and automatic-reset low-pressure switch.

- Refrigerant Charge:  R-410A.

        - Refrigerant Coil:  Copper tube, with mechanically bonded aluminum fins, complying with ARI 210/240, and with liquid subcooler.

        - Heat Pump Components:  Reversing valve and low-temperature air cut-off thermostat.

        - Fan:  Aluminum-propeller type, directly connected to motor.

        - Motor:  Permanently lubricated, with integral thermal-overload protection.

        - Low Ambient Kit:  Permits operation down to 45 deg F (7 deg C).

        - Mounting Base:  Polyethylene.

  - ACCESSORIES

- a. Thermostat:  Low voltage with subbase to control compressor and evaporator fan.

  - Thermostat:  Wireless infrared functioning to remotely control compressor and evaporator fan, with the following features:

  - Compressor time delay.

  - 24-hour time control of system stop and start.

  - Liquid-crystal display indicating temperature, set-point temperature, time setting, operating mode, and fan speed.

  - Fan-speed selection, including auto setting.

  - Automatic-reset timer to prevent rapid cycling of compressor.

  - Refrigerant Line Kits:  Soft-annealed copper suction and liquid lines factory cleaned, dried, pressurized, and sealed; factory-insulated suction line with flared fittings at both ends.

  - ROOF – TOP PACKAGED AIR – CONDITIONING UNITS :

Ambient temp 43 ºC

Shall have two – stage semi – hermetic reciprocating compressors using refrigerant R407

Shall be double skin and suitable for outdoors installation.

A high-quality paint finish shall protect the pre painted steel panels.

The units shall be designed for extremely quiet operation.

Shall have fans to offer a uniform air distribution and maximize coil output.

The units shall offer exceptional installation flexibility.

Units shall have a low noise centrifugal supply and return fans that permit ducted installation with high static pressure.

Units shall include factory-mounted valves  and controls.

The units connection side shall easily be changed form right to left or vice versa.

A high precision, electronic unit control with accuracy of + 0.5K shall be mounted on. The right or left of the unit or on the wall.

The electric connections shall be in a separate control box in a protected location.

A positioning template shall be supplied with the unit to facilitate installation.

Routine maintenance shall be limited to filter cleaning.

The filter shall be installed to be easily accessible for cleaning and maintenance purposes.

Each unit should have a variable speed switch controller and a pro-dialog plus control system which allows programming its operation.

It shall be provided with a mixing box and fresh air, exhaust and return automatic volume dampers and fans to get free cooling (equipped with Economizer. It shall have flat filters (1 inch)

It is operating at 3 phase, 400V and 50Hz. The supply and return fan speed should not exceed 900 RPM.

External over load protection for all compressors and circuit breakers for each motor and main circuit breaker for the unit

It is including all instruments and accessories are included such as valves, dampers, fan speed controller, bracket, hanger's controls, bases and all necessary works as per drawings and as approved by the Engineer.

The unit shall stand with the cooling and heating loads and the air flow rate at the design conditions.

The supply fan should be off during the defrost process when the unit is working for heating.

Each compressor and fan motor should have a circuit breaker, contactor and internal thermal protection.

Each unit should have high and low pressure switches, a differential oil pressure switch, a filter drier, hot gas muffler, a sight glass indicator, solenoid valves, a thermostatic expansion valve, a low ambient controller, a main disconnect switch, a heat pump with suction accumulator.

  - AIR CURTAINS

Air curtain of 15 cm internal wheel as the following :

Air velocity 2 m/sec.

Three speed fan.

Curtain to be installed at the main entrance door

Part 3   EXECUTION

- 3.1INSTALLATION

AC Package Units factory assembled, pre-charged, tested and provided with a single electrical connection point .

On arrival to the job site they are ready to be lifted to their operating position using the lifting supports available on the units.

- A      Install units level and plumb.

- B     Install evaporator-fan components using manufacturer's standard mounting devices      securely fastened to building structure.

- C     Install ground-mounting, compressor-condenser components on (100-mm-) thick,       reinforced concrete base; (100 mm) larger on each side than unit.

- D   Install ground-mounting, compressor-condenser components on polyethylene mounting base.

- E       Install seismic restraints.

- F     Install and connect precharged refrigerant tubing to component's quick-connect fittings.  Install tubing to allow access to unit.

  - CONNECTIONS

- A    Piping installation requirements are specified in other Division 15 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

- B       Install piping adjacent to unit to allow service and maintenance.

- C     Duct Connections:  Duct installation requirements are specified in Division 15 Section "Metal Ducts."  Drawings indicate the general arrangement of ducts.  Connect supply and return ducts to split-system air-conditioning units with flexible duct connectors.  Flexible duct connectors are specified in Division 15 Section 4

- E      Electrical Connections:  Comply with requirements for    power wiring, switches, and motor controls.

  - FIELD QUALITY CONTROL

- Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect, test, and adjust field-assembled components and equipment installation, including connections, and to assist in field testing.  Report results in writing.

- Perform the following field tests and inspections and prepare test reports:

- Leak Test:  After installation, charge system and test for leaks.  Repair leaks and retest until no leaks exist.

- Operational Test:  After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

- Test and adjust controls and safeties.  Replace damaged and malfunctioning controls & equipment.

- Remove and replace malfunctioning units and retest as specified above.

  - STARTUP SERVICE

- Engage a factory-authorized service representative to perform startup service.

- Complete installation and startup checks according to manufacturer's written instructions.

  - DEMONSTRATION

- Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain units.

END OF SECTION

SECTION:  12.00

DEMOSTIC COLD AND HOT WATER SERVICES

## PART 1   GENERAL

This section covers Cold & Hot Water supply to all buildings in the project. It covers, main water connections, underground water tank, cold water filtration system, boosting pumps, hot water circulating pumps, overhead GRP tanks, risers, distribution network, connection to other buildings, heating calorifiers, electric water heaters, & related pipe works.

Purified water services are covered in relevant section for Purified Water Services.

1.1   	SUBMITTALS

The following shall be submitted in accordance with relevant sections for Submittal Procedures:

Shop Drawings

Domestic Cold & Hot Water Supply

Product Data

Pipe and fittings

Valves

Pipe hangers and supports

Pumps

Boosting Pump Sets

Pressure gages

Water meters

Strainers

Backflow preventers

Filters

Sand Filters

Duplex Water Softener

Calorifiers

Thermometers

Test Reports

Backflow Preventers Test Report

Operation and Maintenance Data

1.2   	GENERAL REQUIREMENTS

The cold and hot water systems shall be executed as shown on the drawings, complete with all water distribution piping, water tanks, pumps, etc.

The Contractor shall be responsible for providing the main cold water supply pipe and accessories from the city mains including obtaining the necessary permits, performing all legal matters and making the tie-in to the water source in accordance with local codes, regulations and requirements of the water authorities having jurisdiction and including the provision of the water meter or orifice installation as might be required and as instructed by the authorities or the Engineer, all on his own account.

Underground water pipes shall not be run in the same trench as sewer pipes. Adequate precautions shall be taken for protecting underground water pipes from contamination from any source.

The work also includes providing rough in and making final plumbing connections to equipment furnished under other sections of this specification.

Hot and Cold water system including fixtures, equipment, materials, installation, testing, and workmanship shall be in accordance with the latest version of Health Technical Memorandum HTM 2027, for operational management of Hot and cold water supply, and ICC- Pluming Code except as modified herein. In the codes referred to herein, the advisory provisions shall be considered to be mandatory, as though the word "shall" had been substituted for the word "should" wherever it appears.

1.3   	PROJECT/SITE CONDITIONS

The Contractor shall become familiar with details of the work, verify dimensions in the field, and advise the Engineer of any discrepancy before performing any work.

## PART 2   PRODUCTS

2.1   	Pipes and Fittings

2.1.1   	CPVC Plastic Pipe, Fittings, and Solvent Cement

For all cold & hot water supply inside the building provide CPVC pipes &fittings to ASTM F 441/F 441M, SCH 40 for sizes 50mm &smaller, & SCH 80 for sizes 65mm & larger. Provide male threaded adapters with PTFE (polytetrafluoroethylene) pipe thread paste for threaded connections to valves, strainers, and equipment. Plastic Solvent Cement for CPVC Plastic Pipe shall be to ASTM F 493

2.1.2   	Steel Pipes & Fittings

For all pipe work in & from underground water pump room, on roof & from over-head tanks to Nurse accommodation & Guard Rooms, pipes shall be Steel pipe, seamless galvanized, ASTM A 53/A 53M, Type S, Grade B; and fittings shall be Malleable-iron threaded fittings, galvanized to ASME B16.3. Equivalent galvanized mild steel pipes to BS 1387, medium grade with Malleable iron fittings to EB BS 143 / BS 1256 hot dipped galvanized, shall be permitted to be used.

All Galvanized Steel pipes shall be insulated with 25mm thick rigid PIR sections 35kg/m3 density then wrapped with 8.0 OZ canvas cloth and cladded by aluminum sheets to the Engineer approval.

2.2   	Pipe Insulation Material

Insulation shall be as specified in relevant Section for THERMAL INSULATION FOR MECHANICAL SYSTEMS.

2.3   	Miscellaneous Materials

Miscellaneous materials shall conform to the following:

a.  	Hose Clamps:  SAE J1508.

b.  	Hypochlorites:  AWWA B300.

c.  	Liquid Chlorine:  AWWA B301.

d.  	Gauges-Pressure & Vacuum Indicating Dial Type - Elastic Element:  ASME B40.1.

m.  	Thermometers:  ASTM E 1.  Mercury shall not be used in thermometers.

2.4   	PIPE HANGERS, INSERTS, AND SUPPORTS

Pipe hangers, inserts, and supports shall conform to MSS SP-58 and MSS SP-69.

2.5   	VALVES

Whether shown on drawings or not, valves shall be provided on supplies to each equipment and fixtures, on each branch serving a group of fixtures, on each riser, on each main branch serving any floor, on both sides of each ring and on the middle of each ring. Valves 65mm (2-1/2 inches) and smaller shall be bronze with threaded bodies for pipe. Valves 80mm (3 inches) and larger shall have flanged iron bodies and bronze trim.  Pressure ratings shall be 16-bar for all valves. Grooved end valves may be provided if the manufacturer certifies that the valves meet the performance requirements of applicable MSS standard. Valves shall conform to the following standards:

Butterfly Valves                                  				BS 5155

Cast-Iron Gate Valves, Flanged and Threaded Ends		 	BS 5150/BS 5151

Cast-Iron Swing Check Valves, Flanged and Threaded Ends           BS 5153

Cast Iron Ball Valves for General Service         			BS 5159

Cast-Iron Plug Valves, Flanged and Threaded Ends	            	BS 5158

Bronze Gate, Globe, Angle, and Check Valves       			BS 5154

Steel Valves, globe, globe stop and check valves  			BS 5160

Cast-Iron Globe and Angle Valves, Flanged and Threaded Ends	BS 5152

Backwater Valves                                  				ASME A112.14.1

Vacuum Relief Valves                              				ANSI Z21.22

2.6   	Strainers

All strainers shall be of 16 bar working pressure rating. Strainers shall be Y-type, with 26-mesh stainless steel screen with 0.8mm diameter perforations. Strainers shall be bronze, threaded to BS 21, for sizes up to & including 50mm, & cast iron flanged to BS 4504 for larger sizes.

2.7   	Float Valves

Float valves shall be of all bronze construction including levers and arms, with copper float and shall be suitable for a cold water working pressure of 16 bar.

Float valves shall be of the full bore, equilibrium ball type, designed to close tight against maximum pressure when half submerged. they shall have renewable synthetic rubber valve disk and balancing piston bucket.

Float valves shall conform to BS 1212.

2.8   	Water Filters

2.10.1   General Requirement

The water filters shall be fully automatic type constructed of low carbon steel designed for 6.8 bar working pressure, internally epoxy coated and externally prime coated. Filers capacity and description shall meet, as minimum, the requirements indicated on drawings.

The water filters shall be factory equipped with the following features:-

1.   	Adjustable jack support legs

2.   	Access manhole

3.   	Inlet and outlet pressure gauges

4.   	Air relief valve

5.   	Flanged tank openings

6.   	Face piping system

7.   	Multiport control valve of diaphragm type

8.   	Flow controller and cycle controller

9.   	Pressure differential switch to initiate signal for backwash

The backwash shall be carried out automatically through the control valve when the differential pressure through the filter reaches a valve of 0.8 bar above the clean filter pressure drop value.

The water filters shall be selected for influent suspended solids loads greater than 300 ppm.

2.10.2   Multi-media Sand Filters

Sand filters shall be provided for removal of both heavy sediment and suspended matter from water, as indicated. The filter shall be supplied with a number of media distinctly layered with the coarsest layer at the top and the finest layer at the bottom. The specific gravity and size of various layers shall be selected so that the layers cannot mix but will always stratify in the same order upon backwashing. The filtration rate shall be 52.7 m3/hr/m2 and capable of 10 micron effluent water quality. The backwash rate shall be 39.6 m3/hr/m2. All media shall conform to the requirements of AWWA B100.

2.10.3   Activated Carbon Filters

Activated carbon filter shall be provided for removal of chlorine, sediment and organic substances from water, and to protect the R.o. unit. The filter media shall consist of gradual activated carbon, to the requirements of AWWA B100. The filter shall be with automatic backwashed to keep the bed clean.

2.9   	Duplex Water Softener

The water softener shall be of fully automatic twin type consists of a twin softener with a common brine tank designed for 6.8 bar working pressure, with capacities and all requirements as specified in schedule of equipment.

The twin water softener shall be complete packaged unit factory assembled skid mounted type and fully prepiped and wired systems.

The softener tank shall be constructed of low carbon steel with prime and finish coat exterior and epoxy polymide interior lining. The pressure drop of the water softener shall not exceed the specified values on drawings.

The brine tank shall be of polyethylene construction with dust tight cover, and shall be supplied with the required quantity and quality of salt brine as recommended by the manufacturer.

Water softener shall be factory equipped with the following features:-

1.   	Automatic back wash flow controller

2.   	Cycle controller and flow control

3.   	Multi-port valve diaphragm type

4.   	Brine injector

5.   	Automatic electronic batching type water meter

6.   	Alternator control to maintain one unit on standby or regeneration.

- Automatic timer

- Hardness monitor to analyze the effluent water for hardness content and to signal the need for regeneration.

2.10   	Boosting Pumpset

The Contractor shall supply and install cold water boosting pump sets as shown and detailed on the drawings.

Variable speed pumping system shall provide system pressure by varying speed &number of operating pumps. The factory prepiped & prewired assembly shall be mounted on a steel frame complete with pumps, variable speed drives, motors, & controls. The variable speed drives shall be the oil-filled type capable of power transmission throughout their complete speed range without vibration, noise, or shock loading. Each variable speed drive shall be run-tested by the manufacturer for rated performance, & the manufacturer shall furnish written performance certification. System shall have suppressors to prevent noise transmission over electric feed lines. Required electrical control circuitry and system function sensors shall be supplied by the variable speed drive manufacturer. The primary power controls & magnetic motor controllers shall be installed in the controls supplied by the drive manufacturer. The sensors shall be located in the system to control drive speed as a function of constant pump discharge pressure. Connection between the sensors & the variable speed drive controls shall be accomplished with copper wiring. Controls shall be in NEMA 250, Type 1 enclosures.

The pump set shall be completely fully automatic locally assembled skid mounted unit includes the following features:-

a.   	Three duty pumps and one stand-by pump with their motors.

b.   	Galvanized steel frame

- Suction and delivery manifolds with flanged connections

- Isolating valves and flexible connections on suction and delivery of each pump.

e.   	Check valve on delivery of each pump

f.   	Strainer on suction of each pump

- Pressure gauges, pressure switches and pressure relief valves

- One pressure vessel diaphragm type

- Automatic control panel.

Pressure vessel shall be welded mild steel cylindrical vertical type to BS5169 externally galvanized, internally GRP treated. The pressure vessels shall be provided with pressure gauge, lifting lugs, level gauge, safety valve, drain cock, & inspection manhole.

The pump shall be constructed from cast iron casing, Stainless Steel impeller, and stainless steel shaft. The pump shall be provided with mechanical seals.

The pump motor shall be squirrel cage induction type and rated for continuous operation at ambient temperature not less than 50 Deg C.

The motors shall be variable speed type to maintain constant discharge pressure, totally enclosed fan cooled type with insulation class (F) and IP54 protection and rated for 415 volt, 3-phase and 50 cycle.

2.12.1   Cold Water Booster Pumpset Control Panel

The control panel shall consist of the following:-

1   Starter with overload for each motor.

1   Residual current circuit breaker (for each pump)

1   Set timing relays

1   Hand/off/auto switch for each pump

1   Duty pump selector switch or system mode selection switch

1   Run & trip lamps for each motor

3   Indicating lamps, "Power On", "Low Water", and phase failure

1   Main neutral link

1   Cyclic controller

1   Dry run prevention relay and floats switch in feed tank

1   Set of volt free contacts for DDC interface

Construction of panel to be as per relevant section for Control Systems.

The duty pumps shall start with a 15 seconds time delay (adjustable) between each pump.

The "hand" button shall be spring loaded and shall overide all control circuits (except overload) so that the selected pump can be checked for operation.

The pump set shall operate under the control of pressure switches

The control panel design shall ensure:

a.   	Automatic operation of any combination of duty pumps under the control of pressure switches. The H-O-A switch of standby pump shall be in 'OFF' position in this mode of operation and the duty pumps shall be selected at the duty pump selection switch (P1-P2-P3, P2-P3-P4, P1-P3-P4 or P1-P2-P4).

b.   	Automatic operation of all pumps under the control of pressure switches & cyclic relay. The duty pump selection switch shall be in 'Auto' position.

c.   	Automatic switchover to standby pump in case of failure of duty pump.

d.   	The HAND position of H-O-A switches is only for testing of pump and shall be spring loaded. Alternatively non latching push button shall be used for starting pump in HAND mode.

e.   	Dry run protection based on level switch in the feed tank with indication.

f.   	Volt free terminals for remote indications of common fault including low water level in feed tank and power OFF.

2.11     Steam to Water Hot Water Calorifier

Furnish and install packaged hot water generator / Calorifier (s) of capacity and size as shown on drawings and described in the equipment schedule.

Each packaged generator shall be factory assembled with all necessary controls and trim as specified.

Each unit shall be constructed in accordance with Section VIII of the ASME code for working pressure of 125 PSI.

Manufacturer’s Data Report shall be furnished and certified by a registered National Board Inspector.

The packaged hot water generator shall be equipped with an “Temp” control system of size and capacity required to constantly vary the flow of steam to the heating coil in proportion to the variation in flow and temperature of the domestic

water demands.

Each packaged hot water generator shall be constructed and equipped as follows:

1. Hot water storage section to have a capacity mentioned in the drawings. Vertical Storage section shall be quality carbon steel with stainless steel fittings and tank nozzle for a working

pressure of 125 PSI.

ASME Code storage section to be lined with “Atahco” (A) Cement. Applied by packaged generator manufacturer. The entire inside surface of the pressure

vessel shall be thoroughly cleaned prior to application. The entire surface shall then be coated with a low soluble cement to a minimum thickness of 1/4" for tanks 48" diameter and under, and 3/8" thick for tanks 54" diameter and

over.

The cement shall be of a type that resists corrosion and shall have the same coefficient of expansion as the steel shell. The lining shall have a 5 year warranty as provided by the manufacturer.

2. The storage tank shall be fitted with Two removable type submerged U-tube seamless copper tube (copper/nickel, 304stainless) heat exchanger. Tubes to have heating capacity of full tank size in One hour , using 60 PSI steam pressure. Tube sheet to be carbon steel for design pressure of 150 PSIG.

3. “ Temp” Control system

The package unit shall be furnished with Two steam control valves, one being motorized electrical and the other one Self-acting . Control valves shall

have a steam capacity as requested by the calorifier but not less than steam fittings specification limits.

Other items to be included :

1. Strainer for control valve.

2. Steam Trap on condensate side of coil.

3. Panel Mounted Gages

4. Pressure relief valve

5. In-line all bronze circulating pump

6. Vacuum breaker for steam coil.

7. Steel pipe legs and skid for vertical units.

8. Installation and operating instructions.

9. The package generator shall be insulated with 11/2" fiberglass insulation and covered with a 22 gauge sheet metal jacket.

10. Lifting Lugs

11. Steam pressure gauge with pig tail and shut-off clock.

2.12   	Hot Water Return Pumps

The Contractor shall supply and install the hot water return pumps as shown and detailed on the drawings. The pumps shall be inline close coupled single suction centrifugal type. The pumps shall have suction and discharge flanges of the same diameter and on the same centerline. The pump motor shall be of squirrel cage induction type as indicted, rated for continuous operation at ambient temperature not less than 50 Deg C. The motor shall be totally enclosed fan cooled type with insulation class F and IP54 protection. The motor shall be rated as indicated. The pump construction shall be all stainless steel have a pressure rating not less than 10 bar. Pipe connections including fittings, valves, instrumentations etc. shall be as shown on the drawings.

2.13   	Water Meters

The water meters shall be purchased from Water Authority and paid for directly by the Employer. The Contractor shall be responsible for liaison with Water Authority to ensure that they are available at the programmed time. The Contractor shall include for collecting water meters from WA, their handling, storage, installation, labelling etc.

## PART 3 EXECUTIONS

3.1   	General

Underground water pipes shall not be run in the same trench as sewer pipes. Adequate precautions shall be taken for protecting underground water pipes from contamination from any source.

Piping located in air plenums shall conform to NFPA 90A requirements. Plastic pipe shall not be installed in air plenums. Installation of plastic pipe where in compliance with NFPA may be installed in accordance with PPFA-01. The plumbing system shall be installed complete with necessary fixtures, fittings, traps, valves, and accessories. Water piping shall be extended 1.5m outside the building, unless otherwise indicated. A ball valve and drain shall be installed on the water service line inside the building approximately 150mm above the floor from point of entry. Piping shall be connected to the exterior service lines or capped or plugged if the exterior service is not in place. Sewer and water pipes shall be laid in separate trenches, except when otherwise shown. Exterior underground utilities shall be at least 300mm below the average local frost depth or as indicated on the drawings. If trenches are closed or the pipes are otherwise covered before being connected to the service lines, the location of the end of each plumbing utility shall be marked with a stake or other acceptable means. Valves shall be installed with control no lower than the valve body.

3.2   	Pipework General

All cold water pipework from the mechanical room to the building shall laid inside concrete trench (together with other pipes) as shown on the drawings. Concrete trench details shall be as shown on the structural drawings.

Pipe work inside buildings shall follow the lines of walls vertically & horizontally & shall be graded as necessary for draining & venting. Joints in pipe work shall not be made within walls, or floors and where pipes pass through these structures they shall be sleeved. Where pipes pass through walls, floors, or ceiling exposed to view, they shall be fitted with chrome plated pipe covers. During the course of construction, open ends of pipe work shall be sealed with compression type stop ends. Paper, wood, will not be allowed.

All pipe penetrations of lower and upper deck slabs and planters shall be made with puddle flanges.

All connections of plastic pipes or steel tubes to threaded fittings shall be via adapters. Cut threads shall not be allowed.

3.3   	Utilities

The piping shall be extended to fixtures, outlets, and equipment. The hot-water and cold-water piping system shall be arranged and installed to permit draining. The supply line to each item of equipment or fixture, except faucets, flush valves, or other control valves, which are supplied with integral stops, shall be equipped with a shutoff valve to enable isolation of the item for repair and maintenance without interfering with operation of other equipment or fixtures. Supply piping to fixtures, faucets, hydrants, shower heads, and flushing devices shall be anchored to prevent movement.

3.4   	Cutting and Repairing

The work shall be carefully laid out in advance, and unnecessary cutting of construction shall be avoided. Damage to building, piping, wiring, or equipment as a result of cutting shall be repaired by mechanics skilled in the trade involved.

3.5   	Protection of Fixtures, Materials, and Equipment

Pipe openings shall be closed with caps or plugs during installation. Fixtures and equipment shall be tightly covered and protected against dirt, water, chemicals, and mechanical injury. Upon completion of the work, the fixtures, materials, and equipment shall be thoroughly cleaned, adjusted, and operated. Safety guards shall be provided for exposed rotating equipment.

3.6   	Mains, Branches, and Runouts

Piping shall be installed as indicated. Pipe shall be accurately cut and worked into place without springing or forcing. Structural portions of the building shall not be weakened.  Aboveground piping shall run parallel with the lines of the building, unless otherwise indicated. Branch pipes from service lines may be taken from top, bottom, or side of main, using crossover fittings required by structural or installation conditions. Supply pipes, valves, and fittings shall be kept a sufficient distance from other work and other services to permit not less than 12mm between finished covering on the different services. Bare and insulated water lines shall not bear directly against building structural elements so as to transmit sound to the structure or to prevent flexible movement of the lines. Water pipe shall not be buried in or under floors unless specifically indicated or approved. Changes in pipe sizes shall be made with reducing fittings. Use of bushings will not be permitted except for use in situations in which standard factory fabricated components are furnished to accommodate specific accepted installation practice.  Change in direction shall be made with fittings.

3.7   	Pipe Drains

Pipe drains shall be provided at the bottom of each riser, and shall consist of 20mm (3/4 inch) hose bib with renewable seat and ball valve ahead of hose bib.

3.8 	EXPANSIONS and Contraction of Piping

Allowance shall be made throughout for expansion and contraction of water pipe. Each hot water and hot-water circulation riser shall have expansion loops or other provisions such as offsets, changes in direction, etc., where indicated and/or required.  Risers shall be securely anchored as required or where indicated to force expansion to loops. Branch connections from risers shall be made with ample swing or offset to avoid undue strain on fittings or short pipe lengths. Horizontal runs of pipe over 15m in length shall be anchored to the wall or the supporting construction about midway on the run to force expansion, evenly divided, toward the ends. Sufficient flexibility shall be provided on branch run outs from mains and risers to provide for expansion and contraction of piping.  Flexibility shall be provided by installing one or more turns in the line so that piping will spring enough to allow for expansion without straining.

3.9   	Thrust Restraint

Plugs, caps, tees, valves and bends deflecting 11.25 degrees or more, either vertically or horizontally, in waterlines 100mm in diameter or larger shall be provided with thrust blocks, where indicated, to prevent movement. Thrust blocking shall be concrete of a mix not leaner than: 1 cement, 2-1/2 sand, 5 gravel; and having a compressive strength of not less than 14 MPa after 28 days. Blocking shall be placed between solid ground and the fitting to be anchored. Unless otherwise indicated or directed, the base and thrust bearing sides of the thrust block shall be poured against undisturbed earth. The side of the thrust block not subject to thrust shall be poured against forms. The area of bearing will be as shown. Blocking shall be placed so that the joints of the fitting are accessible for repair. Steel rods and clamps, protected by galvanizing or by coating with bituminous paint, shall be used to anchor vertical down bends into gravity thrust blocks.

3.10   	Connections to Sanitary Fixtures

The connections of CPVC pipes to the tapes, mixers etc., shall be made using elbow/ adapter housed in PVC box (Termination Box) built inside the wall. The boxes shall have provision for incoming flexible conduit.

The termination box shall have one connection for CPVC pipe on one side and female thread for the tap, mixer connection on other.

The connection of elbow to the tap, mixer etc. shall be made using chrome plated angle valve complete with flexible connection

3.11   	Joints

Installation of pipe and fittings shall be made in accordance with the manufacturer's recommendations. Mitering of joints for elbows and notching of straight runs of pipe for tees will not be permitted. Joints shall be made up with fittings of compatible material and made for the specific purpose intended.

3.11.1   Threaded : Threaded joints shall be to BS 21.

3.11.2   Unions and Flanges

Unions, flanges and mechanical couplings shall not be concealed in walls, ceilings, or partitions.  Unions shall be used on pipe sizes 65 mm (2-1/2 inches) and smaller; flanges shall be used on pipe sizes 80 mm (3 inches) and larger.

3.11.3   Plastic Pipe

CPVC pipe shall have joints made with solvent cement elastomeric, threading, (threading of Schedule 80 Pipe is allowed only where required for disconnection and inspection; threading of Schedule 40 Pipe is not allowed), or mated flanged.

3.12   	Dissimilar Pipe Materials

Connections between ferrous and non-ferrous copper water pipe shall be made with dielectric unions or flange waterways. Dielectric waterways shall have temperature and pressure rating equal to or greater than that specified for the connecting piping.  Waterways shall have metal connections on both ends suited to match connecting piping.  Dielectric waterways shall be internally lined with an insulator specifically designed to prevent current flow between dissimilar metals. Dielectric flanges shall meet the performance requirements described herein for dielectric waterways. Connecting joints between plastic and metallic pipe shall be made with transition fitting for the specific purpose.

3.13   	Corrosion Protection for Buried Pipe and Fittings

3.13.1   Steel

Steel pipe, joints, and fittings shall be cleaned, coated with primer, and wrapped with tape. Pipe shall be cleaned, coated, and wrapped prior to pipe tightness testing. Joints and fittings shall be cleaned, coated, and wrapped after pipe tightness testing. Tape shall conform to AWWA C203 and shall be applied with a 50 percent overlap. Primer shall be as recommended by the tape manufacturer.

3.14   	Pipe Sleeves and Flashing

Pipe sleeves shall be furnished and set in their proper and permanent location.

3.14.1   Sleeve Requirements

Pipes passing through concrete or masonry walls or concrete floors or roofs shall be provided with pipe sleeves fitted into place at the time of construction.  Sleeves are not required for supply, drainage, waste and vent pipe passing through concrete slab on grade, except where penetrating a membrane water- proof floor. A modular mechanical type sealing assembly may be installed in lieu of a waterproofing clamping flange and caulking and sealing of annular space between pipe and sleeve. The seals shall consist of interlocking synthetic rubber links shaped to continuously fill the annular space between the pipe and sleeve using galvanized steel bolts, nuts, and pressure plates. The links shall be loosely assembled with bolts to form a continuous rubber belt around the pipe with a pressure plate under each bolt head and each nut. After the seal assembly is properly positioned in the sleeve, tightening of the bolt shall cause the rubber sealing elements to expand and provide a watertight seal between the pipe & the sleeve. Each seal assembly shall be sized as recommended by the manufacturer to fit the pipe and sleeve involved. Sleeves shall not be installed in structural members, except where indicated or approved. Rectangular and square openings shall be as detailed. Each sleeve shall extend through its respective floor, or roof, and shall be cut flush with each surface, except for special circumstances. Pipe sleeves passing through floors in wet areas such as mechanical equipment rooms, lavatories, kitchens, & other plumbing fixture areas shall extend a min. of 100mm above the finished floor. Unless otherwise indicated, sleeves shall be of a size to provide a minimum of 6mm (1/4 inch) clearance between bare pipe or insulation & inside of sleeve or between insulation and inside of sleeve. Sleeves in bearing walls and concrete slab on grade floors shall be steel pipe or cast-iron pipe. Sleeves in nonbearing walls or ceilings may be steel pipe, cast-iron pipe, galvanized sheet metal with lock-type longitudinal seam, or plastic. Except as otherwise specified, the annular space between pipe & sleeve, or between jacket over insulation & sleeve, shall be sealed as indicated with sealants conforming to ASTM C 920 & with a primer, backstop material & surface preparation as specified. The annular space between pipe & sleeve, between bare insulation & sleeve or between jacket over insulation & sleeve shall not be sealed for interior walls, which are not designated as fire rated. Sleeves through below-grade walls in contact with earth shall be recessed 12mm (1/2 inch) from wall surfaces on both sides. Annular space between pipe and sleeve shall be filled with backing material and sealants in the joint between the pipe&concrete or masonry wall as specified above. Sealant selected for the earth side of the wall shall be compatible with dampproofing/waterproofing materials that are to be applied over the joint sealant. Pipe sleeves in fire-rated walls shall be of equal fire rating.

3.14.2   Flashing Requirements

Pipes passing through roof shall be installed through a 4.9 kg per square meter (16 ounce) copper flashing, each within an integral skirt or flange. Flashing shall be suitably formed, & the skirt or flange shall extend not less than 200mm from the pipe and shall be set over the roof or floor membrane in a solid coating of bituminous cement. The flashing shall extend up the pipe a minimum of 250mm. For cleanouts, the flashing shall be turned down into the hub and caulked after placing the ferrule. Pipes passing through pitched roofs shall be flashed, using lead or copper flashing, with an adjustable integral flange of adequate size to extend not less than 200mm from the pipe in all directions and lapped into the roofing to provide a watertight seal. The annular space between the flashing and the bare pipe or between the flashing and the metal-jacket-covered insulation shall be sealed as indicated. Flashing for dry vents shall be turned down into the pipe to form a waterproof joint. Pipes, up to and including 250mm (10 inches) in diameter, passing through roof or floor waterproofing membrane may be installed through a cast-iron sleeve with caulking recess, anchor lugs, flashing-clamp device, and pressure ring with brass bolts. Flashing shield shall be fitted into the sleeve clamping device. Pipes passing through wall waterproofing membrane shall be sleeved as described above. A waterproofing clamping flange shall be installed.

3.14.3   Waterproofing

Waterproofing at floor-mounted water closets shall be accomplished by forming a flashing guard from soft-tempered sheet copper. The center of the sheet shall be perforated and turned down approximately 40mm to fit between the outside diameter of the drainpipe and the inside diameter of the cast-iron or steel pipe sleeve. The turned-down portion of the flashing guard shall be embedded in sealant to a depth of approximately 40mm; then the sealant shall be finished off flush to floor level between the flashing guard and drainpipe. The flashing guard of sheet copper shall extend not less than 200mm from the drainpipe and shall be lapped between the floor membrane in a solid coating of bituminous cement.  If cast-iron water closet floor flanges are used, the space between the pipe sleeve and drainpipe shall be sealed with sealant and the flashing guard shall be upturned approximately 40mm to fit the outside diameter of the drainpipe and the inside diameter of the water closet floor flange. The upturned portion of the sheet fitted into the floor flange shall be sealed.

3.14.4   Pipe Penetrations of Slab on Grade Floors

Where pipes, fixture drains, floor drains, cleanouts or similar items penetrate slab on grade floors, except at penetrations of floors with waterproofing membrane as specified in paragraphs Flashing Requirements and Waterproofing, a groove 6 to 13mm wide by 6 to 10mm deep shall be formed around the pipe, fitting or drain.  The groove shall be filled with a suitable sealant as specified.

3.15   	Fire Seal

Where pipes pass through fire walls, fire-partitions, fire-rated pipe chase walls or floors above grade, a fire seal shall be provided or equal fire rating.

3.16   	Supports

3.16.1   General

Hangers used to support piping 50mm (2 inches) and larger shall be fabricated to permit adequate adjustment after erection while still supporting the load. Pipe guides and anchors shall be installed to keep pipes in accurate alignment, to direct the expansion movement, and to prevent buckling, swaying, and undue strain. Piping subjected to vertical movement when operating temperatures exceed ambient temperatures shall be supported by variable spring hangers and supports or by constant support hangers. In the support of multiple pipe runs on a common base member, a clip or clamp shall be used where each pipe crosses the base support member. Spacing of the base support members shall not exceed the hanger and support spacing required for an individual pipe in the multiple pipe run. Threaded sections of rods shall not be formed or bent.

3.16.2   Pipe Hangers, Inserts, and Supports

Installation of pipe hangers, inserts and supports shall conform to MSS SP-58 and MSS SP-69, except as modified herein.

a.  	Types 5, 12, and 26 shall not be used.

b.  	Type 3 shall not be used on insulated pipe.

c.  	Type 18 inserts shall be secured to concrete forms before concrete is placed. Continuous inserts which allow more adjustment may be used if they otherwise meet the requirements for type 18 inserts.

d.  	Type 19 and 23 C-clamps shall be torqued per MSS SP-69 and shall have both locknuts and retaining devices furnished by the manufacturer. Field- fabricated C-clamp bodies or retaining devices are not acceptable.

e.  	Type 20 attachments used on angles and channels shall be furnished with an added malleable-iron heel plate or adapter.

f.  	Type 24 may be used only on trapeze hanger systems or on fabricated frames.

g.  	Type 39 saddles shall be used on insulated pipe 100mm (4 inches) and larger when the temperature of the medium is 15 degrees C or higher.  Type 39 saddles shall be welded to the pipe.

h.  	Type 40 shields shall:

(1)  	Be used on insulated pipe less than 100 mm (4 inches).

(2)  	Be used on insulated pipe 100 mm (4 inches) and larger when the temperature of the medium is 15 degrees C or less.

(3)  	Have a high density insert for all pipe sizes. High density inserts shall have a density of 128 kg per cubic meter (8 pcf) or greater.

i.  	Horizontal pipe supports shall be spaced as specified in MSS SP-69 and a support shall be installed not over 300mm from the pipe fitting joint at each change in direction of the piping. Pipe supports shall be spaced not over 1.5m apart at valves. Operating temperatures in determining hanger spacing for CPVC pipe shall be 82 degrees C. Horizontal pipe runs shall include allowances for expansion and contraction.

j.  	Vertical pipe shall be supported at each floor, except at slab-on-grade, at intervals of not more than 4.5m nor more than 2m from end of risers, and at vent terminations. Vertical pipe risers shall include allowances for expansion and contraction.

k.  	Type 35 guides using steel, reinforced polytetrafluoroethylene (PTFE) or graphite slides shall be provided to allow longitudinal pipe movement.  Slide materials shall be suitable for the system operating temperatures, atmospheric conditions, & bearing loads encountered. Lateral restraints shall be provided as needed. Where steel slides do not require provisions for lateral restraint the following may be used:

(1)  	On pipe 100mm (4 inches) and larger when the temperature of the medium is 15 degrees C or higher, a Type 39 saddle, welded to the pipe, may freely rest on a steel plate.

(2)  	On pipe less than 100mm (4 inches) a Type 40 shield, attached to the pipe or insulation, may freely rest on a steel plate.

(3)  	On pipe 100mm (4 inches) and larger carrying medium less that 15 degrees C a Type 40 shield, attached to the pipe or insulation, may freely rest on a steel plate.

l.  	Pipe hangers on horizontal insulated pipe shall be the size of the outside diameter of the insulation. The insulation shall be continuous through the hanger on all pipe sizes and applications.

m.  	Where there are high system temperatures and welding to piping is not desirable, the type 35 guide shall include a pipe cradle, welded to the guide structure and strapped securely to the pipe. The pipe shall be separated from the slide material by at least 100mm or by an amount adequate for the insulation, whichever is greater.

n.  	Hangers and supports for plastic pipe shall not compress, distort, cut or abrade the piping, and shall allow free movement of pipe except where otherwise required in the control of expansion/contraction.

3.17   	Disinfection

After operational tests are complete, the entire domestic hot and cold water distribution system shall be disinfected. System shall be flushed as specified, before introducing chlorinating material. The chlorinating material shall be hypochlorites or liquid chlorine.  Water chlorination procedure shall be in accordance with AWWA M20. The chlorinating material shall be fed into the water piping system at a constant rate at a concentration of at least 50 parts per million (ppm). A properly adjusted hypochlorite solution injected into the main with a hypochlorinator, or liquid chlorine injected into the main through a solution-feed chlorinator and booster pump, shall be used. The chlorine residual shall be checked at intervals to ensure that the proper level is maintained. Chlorine application shall continue until the entire main is filled. The water shall remain in the system for a minimum of 24 hours. Each valve in the system being disinfected shall be opened and closed several times during the contact period to ensure its proper disinfection. Following the 24-hour period, no less than 25 ppm chlorine residual shall remain in the system.  Water tanks shall be disinfected by the addition of chlorine directly to the filling water. Following a 6 hour period, no less than 50 ppm chlorine residual shall remain in the tank. If after the 24 hour and 6 hour holding periods, the residual solution contains less than 25 ppm and 50 ppm chlorine respectively, flush the piping and tank with potable water, and repeat the above procedures until the required residual chlorine levels are satisfied.  The system including the tanks shall then be flushed with clean water until the residual chlorine level is reduced to less than one part per million. During the flushing period each valve and faucet shall be opened and closed several times. Samples of water in disinfected containers shall be obtained from several locations selected by the Contracting Officer. The samples of water shall be tested for total coliform organisms (coliform bacteria, fecal coliform, streptococcal, and other bacteria) in accordance with AWWA EWW. The testing method used shall be either the multiple-tube fermentation technique or the membrane-filter technique. Disinfection shall be repeated until tests indicate the absence of coliform organisms (zero mean coliform density per 100 milliliters) in the samples for at least 2 full days. The system will not be accepted until satisfactory bacteriological results have been obtained.

3.18   	TESTS

Tests shall be hydrostatic, unless otherwise specified. Only potable water shall be used for testing. The Employer will supply the test water, but the Contractor shall be responsible for approved disposal of contaminated water.

The Contractor shall ensure that all pipework is completely clear of obstructions, debris, or superfluous matter before any tests are applied. Pipework shall be slowly filled with water, so as to exclude all air. The pipework shall be tested at 10 bar or 1.5 times the maximum pressure in the system (whichever is greater) for a period of two hours without loss.

The Contractor shall give the Engineer 2 working days notice of his intention to test a section of pipework. The Contractor must ensure that each test is witnessed by the Engineer and shall maintain signed test reports for the complete installation.

All items of plant and pipework which are individually pressure tested may be isolated from the system (using blanking plates) for the duration of the test. However, the complete system shall then be pressure tested for working pressure after successful pressure testing as described above.

Record of testing shall be maintained by the Contractor and shall be submitted to the Engineer upon acceptance of the equipment by the Employer.

3.19   	OPERATION AND MAINTENANCE

Contractor shall submit 6 copies of the Operation and Maintenance Manuals 30 days prior to testing of Cold & Hot Water Services. Data shall be updated and resubmitted for final approval no later than 30 days prior to contract completion.

End Of Section

SECTION:  13.00

DRAINAGE, ABOVE GROUND

## PART 1   GENERAL

The work under this section of the specifications shall include all above ground drainage pipe work waste, soil, and rain water, complete with all drains, traps, gullies, cleanouts, vents and all accessories, as shown on the drawings and as specified hereafter.

The above ground drainage pipes shall mean all pipe work inside buildings and located as follows:-

Above floor slab under tiles in walls at high level or low level exposed or concealed all vertical pipes (risers)

1.1   	SUBMITTALS

The following shall be submitted in accordance with relevant sections for SUBMITTAL PROCEDURES:

Shop Drawings

Plumbing System

Detail drawings shall indicate clearances required for maintenance and operation.  Where piping and equipment are to be supported other than as indicated, details shall include loadings and proposed support methods. Mechanical drawing plans, elevations, views, and details, shall be drawn to scale.

Product Data

Plumbing System.

Diagrams, instructions, and other sheets proposed for posting. Manufacturer's recommendations for the installation of bell and spigot joints for cast iron soil pipe.

Test Reports

Certificates

1.2   	STANDARD PRODUCTS

Specified materials and equipment shall be standard products of a manufacturer regularly engaged in the manufacture of such products. Specified equipment shall essentially duplicate equipment that has performed satisfactorily at least two years prior to bid opening.

All pipe jointing and supporting shall be made as recommended by the pipes manufacturer. All pipes and fittings including adapters, couplings and connectors shall be marked with the manufacturer name, standard number and diameter.

1.3   	GENERAL REQUIREMENTS

All works shall be carried out to comply with the current local public health regulations, the latest BS 5572, BS 8301 and current local by-laws and shall be to the entire satisfaction of the Engineer.

1.4   	PROJECT/SITE CONDITIONS

The Contractor shall become familiar with details of the work, verify dimensions in the field, and advise the Engineer of any discrepancy before performing any work.

## PART 2   PRODUCTS

2.1   	General

All pipes and fittings including adapters, couplings and connectors shall be marked with the manufacturer name, standard number and diameter. All pipes and fittings of the same material shall be the standard product of the same manufacturer.

2.2   	UPVC Pipe and Fittings

Unless otherwise indicated, All pipes and fittings used for above ground drainage installations shall un plasticised polyvinyl chloride UPVC and shall conform to BS 4514 and BS 5255,or to ASTM D 2665 and shall be push-fit type with thermoplastic elastomeric rubber ring joint seal to ASTM F 913.

2.3   	Floor TRAP, Drain

Unless otherwise indicated, floor drain type (FT-4) shall be of the same material as pipe, trapped floor gully with 110 mm diameter top socket, three side 65mm inlet sockets, and one 80 mm diameter outlet socket equipped with screwed plug for rodding.

&(FT-4SE) sealed SS cover 20x20cm. Floor drain cover shall be 200mm square SS 304 construction, screw down slotted grating with cover.

Floor drain type FD-4 shall comprise 100mm dia UPVC P-trap and connecting piece provided with 200x200 mm nickel bronze screw down slotted grating with cover.

2.4   	Traps

All traps in wash basins, sinks and floor drain, etc. shall have 75mm water seal. All traps shall have the same bore throughout the trap, connection to the buildings fixed drain shall be via an "O" ring fittings.

2.5   	Roof Drain - Type (RWO)

Roof drain shall be cast aluminum type supplied with socket outlet of size to fit with the rainwater pipes as shown on the drawings.

2.6   	Roof Vent Cowl-Type

Roof vent cowl shall be provided for all vent pipes as shown on the drawings. Roof vent cowl shall be UPVC with screened cap and connected to the vent pipe by solvent welding.

2.7   	Cleanouts

Cleanouts shall be installed, to provide access to waste and soil pipes for inspection or cleaning. All Cleanouts types shall be same as pipe material. Cleanouts shall be provided as shown on the drawings, and at or near the foot of every vertical stack and no long horizontal pipe runs at every 15 meter intervals. UPVC Cleanouts on horizontal pipes (not buried) shall be UPVC access cap fitted with screw cap and washer complete with PTFE tape to seal thread. Cleanouts on horizontal and vertical pipes (not fitted to the fittings) shall be made by access pipe with 75 mm. diameter, opening for access and sealed with screwed cover. All fittings used for the connection between horizontal pipe and vertical pipe (not buried) shall be fitted with access doors secured by two zinc plated screws and captive nuts.

2.8   	Pipe Hangers, Inserts and Pipe Supports

Pipe hangers, inserts, and supports shall conform to MSS SP-58 and MSS SP-69.

## PART 3 EXECUTIONS

3.1   	GENERAL INSTALLATION REQUIREMENTS

All pipes shall be installed as per manufacturer instructions

Piping located in air plenums shall conform to NFPA 90A requirements.  Plastic pipe shall not be installed in air plenums. Sewer and water pipes shall be laid in separate trenches, except when otherwise shown.

All change in direction in drainage pipes shall be gradual and not abrupt. Long sweep fittings and 45-degree fittings type shall be used. All pipes shall be plain ended lengths for seal ring connection to all fittings. All exposed pipes shall be provided with suitable paint for protection against U.V. rays.

3.2   	Joints and Connectors

All joints for above ground drainage pipe work shall be air tight and water tight and care shall be taken to insure that no jointing materials projects inside the bore of the pipe.

Seal ring coupling (expansion joint) fitted with black rubber seal ring shall be provided for each vertical pipe (not embedded) located between every two floors, and for horizontal pipes (not embedded) at 4.0 m. intervals.

The connection of UPVC pipes to all water closets shall be made by WC-connector with solvent weld socket and pan seal socket.

Special UPVC connectors and adapters shall be used for connecting the pipes with dissimilar material of other pipes or fittings such as bottle traps, P-traps of plumbing fixtures.

The connection between vertical pipes and under-ground pipes shall be made by long radius sockets bend fitted with rubber seal rings.

3.3   	Supports

All horizontal pipes (not buried) shall be supported at not more 0.90-m. intervals, at each branch connection, at each change in direction and at each base of vertical pipes.

Vertical pipes shall be supported at a minimum of 1.8-m intervals, and at least two pipe support brackets at the floor height.

All buried pipes shall be supported along their entire length on a clean and well compacted layers of fine sand that not contain any stones.

All hangers and supports shall be of approved types, as recommended by the pipes manufacturer.

3.4   	Water Proofing

Where UPVC pipes pass through roofs, they shall be provided with paddle flange to make watertight seal around the pipes at roof level. The method of water proofing shall be made as per the manufacturer instructions.

3.5   	Testing

The work shall be inspected and tested during installation. All work which will be concealed shall be tested before it is finally enclosed. A final test shall be made upon completion of the work for soundness and performance in accordance with Ministry of Public Works and Housing Code of Practice and BS 5572 for Sanitary Pipework.

End Of Section

SECTION:  14.00

# DRAINAGE, BELOW GROUND

## PART 1   GENERAL

The work under this section of the specifications shall include all underground drainage pipework complete with gullies, traps, cleanouts, manholes, and all accessories, as shown on the drawings.

1.1   	SUBMITTALS

The following shall be submitted in accordance with relevant sections for SUBMITTAL PROCEDURES:

Shop Drawings

Plumbing System

Detail drawings shall indicate clearances required for maintenance and operation.  Where piping and equipment are to be supported other than as indicated, details shall include loadings and proposed support methods. Mechanical drawing plans, elevations, views, and details, shall be drawn to scale.

Product Data

Plumbing System.

Diagrams, instructions, and other sheets proposed for posting.

Test Reports

Certificates

1.2   	STANDARD PRODUCTS

Specified materials and equipment shall be standard products of a manufacturer regularly engaged in the manufacture of such products. Specified equipment shall essentially duplicate equipment that has performed satisfactorily at least two years prior to bid opening.

All pipe jointing and supporting shall be made as recommended by the pipes manufacturer. All pipes and fittings including adapters, couplings and connectors shall be marked with the manufacturer name, standard number and diameter.

1.3   	GENERAL REQUIREMENTS

All works shall be carried out to comply with the current local public health regulations, the latest ICC International Plumbing Code and current local by-laws and shall be to the entire satisfaction of the Engineer.

1.4   	PROJECT/SITE CONDITIONS

The Contractor shall become familiar with details of the work, verify dimensions in the field, and advise the Contracting Officer of any discrepancy before performing any work.

## PART 2   PRODUCTS

2.1   	General

All pipes and fittings including adapters, couplings and connectors shall be marked with the manufacturer name, standard number and diameter. All pipes and fittings of the same material shall be the standard product of the same manufacturer.

2.2   	UPVC Pipe and Fittings

The pipes and fittings shall be unplasticised polyvinyl chloride UPVC, push-fit type with rubber ring seal. Pipe size 110mm and 160mm shall conform to BS 4660, and size 200mm up to 630mm shall conform to BS 5481. Pipes and fittings shall be manufactured with polyproplene seal retaining caps.

2.4   	Gully Trap- (GT)

The gully trap shall be UPVC provided with 110mm dia. P-trap and gulley piece as detailed on the drawings. The gully trap shall be provided with 300x300mm ductile iron cover and frame Grade (B) for gully traps located outside building frame, and with 300x300mm galvanized steel cover (5mm thick) recessed type with brass edging for gully traps located inside building frame. The recessed CI area to be same finish of the surrounding area.

## PART 3 EXECUTIONS

3.1   	GENERAL INSTALLATION REQUIREMENTS

All joints for below ground pipe work shall be made by seal ring expansion joint. All change in direction in drainage pipes shall be gradual and not abrupt. Long sweep fittings and 45-degree fittings shall be used. The installation of pipe work shall be carried out in accordance with the requirements and recommendations of BS. code of Practice BS 5955 Part (6)-1980.

Connections to manholes and city sewers shall be made in a completely watertight and approved manner.

Any connections to existing systems shall be made with minimum disturbance to the existing lines. Any existing pipelines or structures which are damaged while making connections shall be replaced or reconstructed to the satisfaction of the Engineer and without any cost to the Employer.

Pipes shall be kept clean until final acceptance of the work. Exposed ends of all incompleted lines shall be closed with wooden plugs and adequately secured at all times when pipe laying is not actually in progress.

Pipes shall be installed on a good foundation and adequate means taken to prevent settlement. Pipes laid in trenches shall be provided with a solid uniform bearing throughout the entire length.

Pipes shall not be burried at less than 600 mm below finished grade for protection against mechanical damage. Pipes shall not be run closer than 1 m. to building bearing walls and footings for protection against building settlement.

All pipes shall be laid to a uniform slope as shown on the drawings. The free vertical drop of a sewer pipe into a new or an existing manhole shall be limited to 450 mm. between the invert level of the pipe opening and the bottom of the manhole. Where conditions necessitate that the drop would exceed 450 mm a drop manhole shall be used, of detail as shown on the drawings.

Trenches shall be kept free of water by pumping, use of well points, under drains or other approved means during pipe laying operations so that all pipe joins are made in the dry. Precautions shall be taken to protect incompleted work from floating due to storms or from any other cause. All pipe lines or structures not stable against uplift during construction shall be well braced or otherwise protected.

All joints shall be inspected and an inspection of the lines as a whole shall show all pipes to be true to line and grade with full circle visible at the manholes. If on inspection the completed sewer or any part thereof shows any structures, pipes or joints which are defective, the defective work shall be replaced or repaired as directed.

3.2   	Excavation for Pipe Lines

a.   	Trenches for pipes shall be excavated to a sufficient depth to allow a 100 mm. minimum bed below the underside of the pipe.

b.   	Trench width shall not be less than the outer diameter of the pipe plus 300 mm and not wider than necessary.

c.   	The sides of trenches, manholes and other excavations shall be adequately supported at all times.

d.   	Any material excavated in forming pipe drains shall, if found unsuitable, be run to spoil and replaced with suitable approved material. All suitable excavated material shall be used as backfill except in French drains.

e.   	Where drain trenches are to be excavated beneath foundations or below the level of adjacent foundations, the sides of the excavation shall be supported by such substantial planking and strutting as steel trench sheeting driven plumb in advance of the excavation proceeding. The trench sheeting shall be carefully withdrawn after compaction of the backfill material so as to cause the minimum disturbance to the backfill and adjacent ground.

3.3   	Bedding and Surrounding of Pipes Beneath Building

a.   	All pipes shall be bedded on 20 N/mm. concrete and shall be supported at the concrete cradles placed behind the sockets or on each side of the joint by methods approved by the Engineer. The supports shall be provided with soft contact padding such as roofing felt or other approved material.

b.   	The annular gaps in flexible joints shall be sealed with approved means to prevent the intrusion of concrete. The pipes to be in contact with concrete shall be washed clean of any mud or clay.

c.   	Concrete shall be gently and evenly placed over the entire width of the trench of bedding as shown on the drawings, & to within 25mm. of the bottom of the pipe. Then, without stopping, it shall be placed gently on the side of the pipe only and carefully worked under the pipe, ensuring that no voids are left below the pipe. Concrete shall the be brought up equally on each side of the pipe to the required finished height, care being taken not to force the pipes off their supports.

d.   	No fill material shall be placed over the concrete until the concrete has reached a crushing strength of 14 N/mm2. The concrete and the pipes shall be kept damp and protected from sun or frost until the concrete has reached the required strength for filling to take place.

3.4   	Bedding and Laying Out of Drain Pipes - External

a.   	Immediately following the trench excavation, the pipes shall be laid and jointed on pipe bedding material.

b.   	The pipes shall be laid so that one is in contact with the bed throughout the length of its barrel. Bedding material being scrabed away at each socket so that the socket does not hear on the bed. Pipes and channels shall be laid with the sockets leading up the gradient. All drainage runs shall be commenced at the point of outfall or at a manhole.

3.5   	Bedding and Surround of Pipes - Generally

After jointing the pipes, the bedding shall be brought up equally on both sides of the pipe, first to the level of the centre of the pipeline and then up to a height of 300mm. above the top of the pipe barrel. This material shall be placed in layers not exceeding 150mm. in thickness and shall be carefully compacted with wooden rammers.

3.6   	Backfilling of Trenches

a.   	All backfilling shall, as far as practicable, be undertaken immediately after the specified operations preceding it have been completed.

b.   	The backfilling shall be undertaken only after completion of testing for such pipes as described herein. From 300 mm. above the barrel of the pipe up to the formation level of the road, the filling in the trench shall continue with selected approved material from excavations, in layers not exceeding 150 mm. in thick. Each such layer shall be solidly rammed before the next layer is added.

c.   	Where the drain does not run under a road, the backfill material shall be solidly rammed up to the existing ground level in the manner described above.

3.7   	Manholes, Sump PITS

3.7.1   	General

Manholes shall be of poured in place reinforced concrete construction & shall be of details shown on the drawings & as per relevant specifications for Cast In Place - Civil.

Manholes shall be constructed to the required depth. The manholes top shall have a 600x600mm clear opening and shall be shaped to accommodate a standard size manhole frame and cover.

Manhole floors shall be formed by hand with rich cement mortar to the size and shape of the sewer. Inverts shall have a cross section of exact shape as the sewers and all changes in sewer size shall be made gradually and evenly. The floor shall have a gradual slope from the side walls to the central channel.

The manhole internal walls shall be plastered with two coats of cement mortar, one part cement to three parts sand, to a total thickness of 15 mm.

During construction of the manhole, galvanized iron steps shall be furnished and set in place on the inside wall. They shall be properly embedded in the wall.

All work shall be carried out in a manner to ensure watertight construction. If leaks occur they shall be caulked, repaired or the entire work shall be removed and rebuilt. Attention shall be particularly paid to the necessary of keeping the water level below all parts of the manhole until the cement has obtained adequate set.

3.7.2   	Benching and Inverts of Manholes

The open channel in the bottom of the manholes shall be formed in the benching with half round of pipe. All side branches shall be connected to the main channel so that the discharge is in the direction of the flow in the main channel. The benching shall be concrete and shall rise vertically from the edge of the channel pipe to a height not less that the outgoing pipe and be sloped upwards from there to meet the wall of the manhole at a gradient of about 1 in 6. Rendering to benching shall be applied in a coat of cement mortar (1:1) to a final thickness of 20mm trowelled to a smooth hard finish in accordance with BS CP-301.

3.7.3   	Temporary Covers for Manholes

Temporary covers shall be fitted and retained in position on all manholes from the time the top access is formed or the concrete cover slab installed, until the permanent cover is installed.

3.7.4   	Manhole Step Irons

All manholes of depth greater than 1200 mm shall be provided with galvanized step irons complying with BS 1247. They shall be staggered in two vertical runs at 300 mm. centers vertically and 225 mm horizontally.

The top iron shall be no more than 350 mm below the underside of the manhole cover slab and the lowest no more than 300 mm above the benching. Manhole cover frames shall be bedded in 1:3 sulphate resisting cement sand mortar.

3.7.5   	Frames and Covers

The Contractor shall provide for each manhole ductile iron frame & cover with a 600mmx600mm clear opening. The concrete masonry shall be neatly and accurately brought to the dimensions of the base of the frame. The frame shall be thoroughly embedded in mortar & frame & cover set level & to the proper grade.

All castings for frames and covers shall be of tough grey iron and shall be made accurately to dimensions and machined to provide even bearing surfaces. Covers shall fit the frames in any position and if found to rattle under traffic shall be replaced. No plugging, burning in or filling to obtain tight covers will be allowed. All castings shall be carefully coated inside and outside with coal tar pitch varnish of approved quality.

All frames and covers shall comply with BS 497 of grade as indicated on the manholes schedules. All manholes covers shall be provided with at least two keyways, for each type of manhole and gully trap covers. All covers and frames shall have clearly cast thereon the number of BS and the appropriate grade.

For dry type manholes, the cover and frame shall be of 600x600mm galvanized steel (5mm thick) with brass edging, recessed type with same material finish on recessed CI surface.

3.7.6	Internal Manholes

All internal manholes shall be bolted double seal type with stainless steel covers and frames, recessed type and shall be of the same finish of the surrounding area.

3.7.7   	Testing of Manholes & Sump Pit

Manholes shall be subjected to a hydraulic test. Pipe stoppers shall be inserted into all pipe ends and the manhole filled with water to a height of 300 mm above the highest point of the benching. This water shall stand for five minutes and then be topped up as necessary. The water shall then remain at this level for a further ten minutes to satisfy the test. If the water level falls, then all defects shall be made good to the satisfaction of the Engineer, and the test shall be repeated as many times as may be necessary until the manhole is satisfactory.

3.7   	GREASE INTERCEPTOR

Large capacity Acid resistant coated interior and exterior fabricated steel grease interceptor, rated as shown in the schedule of equipment with internal air relief by pass, bronze cleanout plug and visible double wall trap seal with removable pressure equalizing/flow diffusing baffle and sediment tray. Gasket non-secured cover with covered recessed lift handle complete with flow control fitting. Regularly furnished with inlet and outlet in high position

3.8         SOLID TRAPS

Solid Interceptor shall be of large capacity Acid resistant epoxy coated interior and

exterior fabricated of steel, Solid Interceptor shall be provided with non-skid secured

cover, and with ready removable stainless lint intercepting basket assembly and

permanent primary straining baffle. Regularly furnished with inlet and outlet in high

position.

PART 4 - SUMP PUMPS

- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

      - SUMMARY

        - This Section includes the following sump pumps and accessories, inside the building, for building storm drainage systems:

          - Submersible sump pumps.

          - Sump pump basins.

        - Related Sections include the following:

          - Division 15 Section "Sewage Pumps" for application in sanitary drainage systems.

      - SUBMITTALS

        - Product Data:  For each type and size of sump pump specified.  Include certified performance curves with operating points plotted on curves, and rated capacities of selected models, furnished specialties, and accessories.

        - Shop Drawings:  Diagram power, signal, and control wiring.

        - Operation and Maintenance Data:  For each sump pump to include in emergency, operation, and maintenance manuals.

      - QUALITY ASSURANCE

        - Product Options:  Drawings indicate size, profiles, and dimensional requirements of sump pumps and are based on the specific system indicated.  Refer to Division 1 Section "Product Requirements."

        - Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

      - DELIVERY, STORAGE, AND HANDLING

        - Retain shipping flange protective covers and protective coatings during storage.

        - Protect bearings and couplings against damage.

        - Comply with pump manufacturer's written rigging instructions for handling.

- PART 2    PRODUCTS

- 2.1   MANUFACTURERS

- In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

          - Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

          - Available Manufacturers:

            - ABS Pumps, Inc.

            - Barnes; Crane Pumps & Systems.

            - Bell & Gossett Domestic Pump; ITT Industries.

            - BJM Corporation.

            - Federal Pump Corp.

            - Gorman-Rupp Company (The).

            - Goulds Pumps; ITT Industries.

  - SUBMERSIBLE SUMP PUMPS

- A   Description: Factory-assembled and -tested, duplex, single-stage, centrifugal, end-suction, submersible, direct-connected sump pumps complying with UL 778 and HI 1.1-1.2 and HI 1.3 for submersible sump pumps.

- B    Casing and Impeller:  Cast-iron casing with metal inlet strainer and brass, bronze, or cast-iron impeller.

- C   Casing and Impeller:  Cast-iron or plastic casing with inlet strainer and metal or plastic impeller.

        - Pump and Motor Shaft:  Stainless steel, with factory-sealed, grease-lubricated ball bearings and double-mechanical seals.

        - Motor:  Hermetically sealed, capacitor-start type, with built-in overload protection; three-conductor waterproof power cable of length required, and with grounding plug and cable-sealing assembly for connection at pump.  Comply with requirements in Division 15 Section "Motors."

          - Moisture-Sensing Probe:  Internal moisture sensor with moisture alarm.

        - Pump Discharge Piping:  Factory or field fabricated, bronze pipe.

        - Basin Cover:  Cast iron or steel with bituminous coating and strong enough to support controls.

        - Controls:  NEMA 250, Type 1 enclosure, pedestal mounted unless wall mounting is indicated; with three micropressure switches in NEMA 250, Type 6 enclosures; mounting rod; and electric cables.  Include automatic alternator to alternate operation of pump units on successive cycles and to operate multiple units if one pump cannot handle load.

          - Float Guide:  Pipe or other restraint for floats and rods in basins of depth greater than 60 inches (1500 mm).

          - High-Water Alarm.

- 2.3  FLEXIBLE CONNECTORS

        - Description:  125-psig (860-kPa) minimum working-pressure rating and ends matching pump connection:

          - Stainless-Steel Flexible Connectors:  Corrugated, stainless-steel inner tubing covered with stainless-steel wire braid.  Include stainless-steel nipples or flanges, welded to tubing.

- PART3  EXECUTION

      - EXAMINATION

        - Examine roughing-in of plumbing piping to verify actual locations of storm drainage piping connections before sump pump installation.

      - SUMP PUMP INSTALLATION

        - Excavating, trenching, and backfilling are specified in Division 2 Section "Earthwork."

        - Install sump pumps according to applicable requirements in HI 1.4.

        - Install pumps and arrange to provide access for maintenance including removal of motors, impellers, couplings, and accessories.

        - Suspend wet-pit-mounted, vertical sump pumps from basin and pit covers.  Make direct connections to storm, drainage piping.

        - Set submersible sump pumps on basin floor.  Make direct connections to storm drainage piping.

        - Install sump pump basins and connect to drainage piping.  Brace interior of basins according to manufacturer's written instructions to prevent distortion or collapse during concrete placement.  Set basin cover and fasten to basin top flange.  Install cover so top surface is flush with finished floor.

        - Construct sump pump pits and connect to drainage piping.  Set pit curb frame recessed in and anchored to concrete.  Fasten pit cover to pit curb flange.  Install cover so top surface is flush with finished floor.

        - Install packaged, pedestal, drainage pump units and make direct connection to storm drainage piping.

        - Install packaged, submersible, drainage pump unit basins on floor or concrete base unless recessed installation is indicated.  Make direct connections to storm drainage piping.

        - Support piping so weight of piping is not supported by pumps.

      - CONNECTIONS

        - Piping installation requirements are specified in Division 15 Section "Storm Drainage Piping."  Drawings indicate general arrangement of piping, fittings, and specialties.

        - Install piping adjacent to sump pumps to allow service and maintenance.

        - Connect storm drainage piping to pumps.  Install discharge piping equal to or greater than size of pump discharge piping.  Refer to Division 15 Section "Storm Drainage Piping."

          - Install flexible connectors adjacent to pumps in discharge piping.

          - Install check and shutoff valves on discharge piping from each pump.  Install unions on pumps having threaded pipe connections.  Install valves same size as connected piping.  Refer to Division 15 Section "Valves" for general-duty valves for drainage piping.

        - Ground equipment according to Division 16 Section "Grounding and Bonding."

        - Connect wiring according to Division 16 Section "Conductors and Cables."

      - STARTUP SERVICE

        - Engage a factory-authorized service representative to perform startup service.

          - Complete installation and startup checks according to manufacturer's written instructions.

          - Verify bearing lubrication.

          - Disconnect couplings and check motors for proper direction of rotation.

          - Verify that each pump is free to rotate by hand.  If pump is bound or drags, do not operate until cause of trouble is determined and corrected.

          - Verify that pump controls are correct for required application.

        - Start pumps without exceeding safe motor power:

          - Start motors.

          - Open discharge valves slowly.

          - Check general mechanical operation of pumps and motors.

        - Test and adjust controls and safeties.

        - Remove and replace damaged and malfunctioning components.

          - Pump Controls:  Set pump controls for automatic start, stop, and alarm operation as required for system application.

          - Set field-adjustable switches and circuit-breaker trip ranges as indicated, or if not indicated, for normal operation.

        - Occupancy Adjustments: When requested within 12 months of date of Substantial Completion, provide on-site assistance in adjusting system to suit actual occupied conditions. Provide up to two visits to Project outside normal occupancy hours for this purpose.

PART 5   	Testing of Drains

a.   	The Contractor shall provide the necessary labour and equipment and include in his Tender for testing and work to the requirements and satisfaction of the Engineer and all relevant public authorities.

b.   	Drains shall be tested by either water or air as directed by the Engineer and the results of the test must be approved by the Engineer before concerting. A further test shall be carried out after backfilling of excavations. the test shall be carried out in the manner described in the following paragraph.

c.   	To facilitate the general building programme, tests shall be made of sections as the work proceeds, such testing however will not absolve the Contractor from his liability for any subsequent or final testing.

d.   	Any defects that become apparent during these tests of any part or parts of the installation shall be rectified at the Contractor's expense and the part, or parts, retested to the satisfaction of the Engineer and the relevant public authorities.

e.   	For a water test, the drain lines shall be subjected to test pressure of at least 1500mm. head of water at the highest point of the section under test. Allowance should be made for added water until absorption has ceased, after which the test proper should be commenced and the water level be maintained for a minimum of 30 minutes without the addition of further water.

f.   	For an air test, a gauge in the form of a glass 'U' tube shall be provided and connected to the drain plug of the length of drain under test. Air shall be pumped into the length of drain until a pressure equivalent to 100 mm. head of water is indicated on the gauge. Without further pumping, pressure should not fall below 75 mm. during the period of five minutes.

g.   	Test for straightens and obstruction shall be made to the Engineer's satisfaction and in accordance with the requirements of BS CP-301, Building Drainage.

h.   	The whole of the installation shall be left clean and free from debris.

j.   	The Contractor shall keep a record of the tests carried out on the drainage installation throughout the Contract, recording date of test, by whom tested and the result, one copy of the records shall be sent to the Engineer on completion of the Contract.

Local Regulations

All works shall be carried out to comply with the current local public health regulations, the latest BS 5572/ BS 8301, Ministry of Public Works and Housing Code of Practice for Sanitary Pipe work and current local by-laws and shall be to the entire satisfaction of the Engineer.

End Of Section

SECTION:  15.00

###### PLUMBING, FIXTURES

PART 1   GENERAL

This section covers the requirements for Sanitary Fixtures. The designation for each fixture is referenced in The Architectural Book of Details and B.O.Q. Where reference is made to Medical Equipment Specifications; the same shall be sought for referenced specifications.

1.1   	SUBMITTALS

The following shall be submitted in accordance with relevant sections for Submittal Procedures:

Shop Drawings;

Plumbing Fixtures;

Product Data

Fixtures;

Fixtures and Fixture Trimming; and

Plumbing Fixture Schedule with catalog cutts of specified plumbing fixtures, valves, related piping system and system location where installed.

1.2   	GENERAL REQUIREMENTS

The Contractor shall furnish and install all the sanitary fixtures as shown on the layout plan drawings and architectural detail plans and as specified below, complete with all their trim and accessories as specified. Prefix numbers identify and locate the fixtures on the Drawings relative to the fixtures described herein.

Sanitary fixtures shall be of vitreous china to BS 3402, unless otherwise specified and of colour as specified. Fixtures shall have smooth glazed surface free from warp, cracks, flaws, discolouration or other imperfections. Imperfect fixtures will not be accepted.

Sanitary fixtures shall be supplied complete with all required metal trim and accessories, as specified, including but not necessarily limited to faucets, wastes, traps, supplies, stop valves, wall flanges, hangers, plates, brackets, anchors, supports.

All exposed piping and metal trim for the sanitary fixtures shall be chrome plated brass to BS 5750; Part (1) with polished finish.

All vitreous china accessories shall match the sanitary fixtures and shall be of the same manufacture and colour.

All sanitary fixtures, trim and accessories shall be the product of a reputable and approved manufacture and as far as practicable shall be procured from one manufacturer unless specified otherwise.

Sanitary fixtures and their trim and accessories shall be installed in a neat, finished and uniform manner as directed by the Engineer. They shall be set straight and true and securely attached to the supporting surfaces. Roughing shall be accurately laid out to conform with finished walls and floors.

The colour of sanitary fixtures shall be white for all fixtures unless other wise directed by the architect.

Sanitary fixtures shall be connected to the drain and water supply pipes in an approved gastight and watertight manner and as detailed on the Drawings.

Strap or padded wrenches shall be used on chrome plated pipe, fittings, valves & other trim.

Sanitary fixtures, metal trim and accessories shall be thoroughly cleaned of labels, plaster, paint droppings and all foreign matter and shall be well polished and tested for perfect working condition before turning them over to the Employer.

Concealed brackets, hangers and plates shall be painted as directed by the Engineer.

The Contractor shall submit to the Engineer a list of all fixtures, trim and accessories that he proposes to use indicating manufacturer, type and model number, with descriptive catalogues clearly marked as to the item proposed.

The Contractor shall submit samples of all fixtures, trim and accessories when asked to do so by the Engineer. The Contractor shall not charge the Employer with the cost of such samples nor shall he use any item different from the approved sample.

1.3   	PROJECT/SITE CONDITIONS

The Contractor shall become familiar with details of the work, verify dimensions in the field, and advise the Engineer of any discrepancy before performing any work.

PART 2   PRODUCTS

2.1   	 WATER CLOSET (WC) WALL Mounted with Flushing Tank

White vitreous china siphon jet action, elongated bowl, 40mm back spud, complete with the following trim and accessories or approved equal:-

- Pan size shall be 400 mm wide x 520 mm deep and shall be complete with easy clean high quality seat and cover manufactured from high impact resistant copolymers.

- Solid plastic seat without cover of same color as water closet, hygienic open front design with metal hinge, rubber washers and plastic screws and nuts.

- Closed coupled 7.5 liter cistern complete with fittings and side connections.

- Chrome plated cistern lever to suite the cistern position.

- Toilet paper holder, ref..

- 110mm push fit on to WC plastic outlet connector.

- Horizontal Grab Bar, ref.

- Tap & Hand Spray, ref.

- 2.2	LAVATORY  COUNTERTOP (Cafeteria toilets)

        - White vitreous china lavatory, as Villeroy & Boch model Ivana No. 614700 under counter, with mixer, complete with fixing brackets.

Lavatory shall be complete with the following trim and accessories, or approved

equal:

          - Lavatory mixer in public toilets & Block B (Typical Floors): 15mm single hole chrome plated mixer, sensor operated, anti blocking safety system, adjustable flow and temperature complete with filter and non return valve.  Mixer to be similar to model Binoptic Mix from DELABIE Grohe or approved equal.

          - Chrome plated 1"1/4 P-trap with wall tube and wall flange, adjustable type.

          - Chrome plated 1/2" angle supply and stop valve with 30 cm long tube, blue index.

          - Chrome plated 1/2" angle supply and stop valve with 30 cm long tube, red index.

2.3         WASH BASIN (Patients Bed Rooms)

- For toilets, vitreous China,wall mounted (Semi-pedestal), white, 50x40 cm,

- mounted on specially designed standard concealed cast iron or steel

- brackets

- bolted to wall, self drained recess for soap, the price includes:-

- -  PVC traps, with overflow connection.

- -  Chrome plated outlet.

- -  Rubber cap fixed to a chrome plated

- Chain.

- Rubber adaptor for connection to the

- wall 2” drain pipe.

- Mixer with gear type operated lever (USA or European origin) chrome plated

- capable of supplying not less than 0.15 l/s at 1 bar,   with noise level not

- exceeding 35 db at 1 m, and to be approved by the engineer.

- Chrome plated copper connection to the angle valves, with two 1/2” angle valves.

- 65x50cm wall mounted mirror, of best quality first choice material,

2.4  	shower tray;

White vitreous china receptor, 900x900x145mm deep with high grade gel coat finish and 50mm corner drain opening, complete with the following trim and accessories or approved equal:

- 40 mm chrome plated grid waste fitting.

- Chrome plated recessed shower controller with flexible tube to hand spray mounted on vertical slide bar. The controller shall have instantaneous reaction to pressure fluctuations to maintain selected temperatures.

- Shower mixer valve set complete. Ref., designed to deliver water at a rate of 37.8 liters per min. (10 gpm) based on a water pressure of 310 kPa (45 psi) at a maximum temperature of 41 degrees C (105 degrees F).

- 15 mm angle inlet connectors.

- Towel rail, ref. (SF-9)

- Soap dish, ref. (SF-15)

- Shower Curtain, ref. (SF-25)

- Shower Curtain Track, ref. (SF-26)

- Fold Down Shower Seat, ref. (SF-2) – (for Patient Rooms)

- Satin aluminum coat hook.

2.4.1   	Shower Mixer Valve

Concealed thermostatic valve in chromium plate. Dual control valve to control temperature of water and flow of water separately. To be made from dezincification resistant brass (DZR). Valve shall be designed to deliver water at a rate of 37.8 liters per min. (10 gpm) based on a water pressure of 310 kPa (45 psi) at a maximum temperature of 41 degrees C (105 degrees F). Water supplies shall be fitted with flow limiters in accordance with manufacture's instructions. It shall be complete with inlet swivel elbows incorporating single non-return valves with compression nuts and rings for 15-mm dia, copper tube.

To include also dual function hand spray chrome plated flexible hose and rail with wall outlet for use with concealed mixer.

2.5   	Wash Basin (Staff Toilets);

The wash basin shall be made of white vitreous china wall mounted type with semi pedestal/trap cover, wash basin with overflow and one tap hole, complete with the following trim & accessories, one hole single lever basin mixer 15mm projection 117mm pop-up waste, tubing trap 32mm and two angle valves with escutcheon 15mm and all necessary accessories. The overall dimension shall be 590 mm x 440 mm.

2.6   	Kitchen and MILK PREPARE Sink

Stainless steel kitchen sink shall be single or double bowl and drainer as

specified or shown on the Drawings. Stainless steel shall be type 304 and 1.6-

mm thickness. The sink shall be provided with three tap holes for pillar mixer,

chain stay hole and overflow and with back splash end.

The sink shall be complete with the following trim and accessories:

- 40-mm dia. chrome plated waste with stainless steel grating and chain stay & plug.

- 40-mm plastic bottle trap with extension tube.

- Flexible plastic tube for overflow connection.

- 15-mm dia. chrome plated angle valves with flexible copper tube and wall flange.

- 15-mm dia. chrome plated pillar mixer with swivel spouts projection 210-mm.

2.7  	Wash Basins (No overflow);

Shall be white vitreous china overall size 365mmx255mm with single tap hole (LH or RH in accordance with location & as directed by engineer on site) no overflow no chain hole complete with single lever C.P. mono block mixer (non pop-up waste) with ceramic disc cartridge and with 1 in (28-mm) CP waste, bottle trap C.P. tail and flange at wall entry.

  - Scrub Up Sink;Ref (Scr.1), (Scr.2)

Specialized factory produced scrub-up sink polished Stainless Steel 304, to

BS1449 part 2 : 1983 , wall mounted, similar to ARMITAGE SHANKS

model S2852 (54161LW) (SU-H1).fixation by Stainless Steel screws, the

length of the unit shall be 160cm, with left hand outlet and strainer waste, 1.5"

plastic resealing bottle trap cover.

The price includes:-

- 2 wall mounted pedestal operated medical type polished St. /St. Liquid soap

- Dispensers (two or one) one Liter. capacity.

- Rubber adaptor for connection to the wall 2” drain pipe. Horizontal spray outlet capable of supplying not less than 0.3 l/s at 3 bars

- Two or one of wall mounted medical scrub-up type mixers, fully exposed    markwik

- 1/2" elbow lever operation type, with noise level not exceeding 35db at 1m.

2.9  	Paper Towel Dispenser; ref

Paper towel dispenser dispenses 300 C-fold or 400 multi-fold paper towels, & shall be made of 304 stainless steel satin finish. Rough wall opening 300 mm-Wx450mm-Hx100 mm-D.

2.10   	Hook Strip; Ref (sf-8)

This shall be made of stainless steel, and shall be satin finished. The hook shall be 25 mm-W and 165 mm-H and projecting 57 mm from wall. It shall be mounting trip 102 mm-H x 610 mm-L with 3 hooks

2.11   	Rail Towel Surface Mounted;)

Stainless steel grab bar for towel holding. Bar dia 25 mm. Bar gauge 18 with concealed mounting plate.

2.12   	Dispenser Toilet Paper;

Recessed toilet paper holder with hood for two roll anchor lugs satin finish. Wall opening 140 mm-W x 140 mm-H x 75 mm-D.

2.13   	Grab Rail - Wall to Floor With Socket;

18 gauge Type 304 stainless steel diameter 813 mm. Satin finish 4 set screws, concealed mounting 840 mm, high.

2.14   	Horizontal Grab Bar (Wall Side);

This shall be made of 18 gauge Type 304 stainless steel diameter 32 mm. satin finish, 4 set screws and concealed mounting 1320 mm. long.

2.15   	Range of Basins Public Toilets;)

Shall be made of high performance homogeneous non-porous thermoset polymer (methyl methacrylate or similar) densely filled with mineral or aluminum tryhydrate such as corian or fountainhead or similar / equal and approved material.

They shall comprise bowls, size 555 x 405 set in to sanitary worktop with front fascia all as one smooth integrated unit. Each bowl shall have one overflow and one tap hole and numbers of basins and details shall be as per the relevant drawings. Each bowl shall be complete with single lever CP. monobloc mixer with pop-up waste and with ceramic disc cartridge and 1 -in (28-mm) CP waste bottle trap, CP tail and flange at wall entry.

2.16   	Mirror Shelf Combination;

The rest resistant angle frame mirror above, furnished with one piece integral shelf. Shelf projects 125mm. & has 20mm. edges on front and sides, Front return edges hemmed for maximum rigidity and safety. Corners are heliarc welded, ground and polished smooth. Shelf manufactured of Type304 stainless steel with satin finish. Concealed 16 gauge stainless steel brackets attach shelf to mirror frame.

2.17   	Soap Dish;

The one piece soap dish shall be made of stainless steel and shall be welded to support arm and flange. It shall have drain holes and two ridges to support bar of soap. The dimensions shall be 115 mm. w. x 50 mm. H. projects 86 mm. from wall.

2.18   	Soap Dispenser (Liquid);

Recessed soap dispenser with drawer type soap vessel, unit type. It shall be made of 304 stainless steel with exposed surface satin finish. It shall have a tumbler lock chrome plated non corroding valve to dispense soap, lotions, and detergents. Also it shall have unbreakable refill window. Wall opening shall be 213 mm x 110 mm H x 100 mm D.

2.19  	Shower Curtain;

This shall be vinyl shower curtains, opaque, matte white vinyl 0.2mm. thick, Nickel plated brass grommets along top, one every 150mm. Bottom sides hemmed 12 hooks required. Length 1600mm.

2.20   	Shower Curtain Track;

Shall be anodized aluminum track 36-mm x 14-mm, plastic glider/hooks, wall support fixings. Hanger at 90o bend of track shall be comprise threaded ceiling support stud, hanger and sleeve.

2.21   	Dirty unit Sink

Stainless steel 304, 60x60cm and 65cm in depth, 2 tapholes at 20cm centers, with one

bowl and without overflow, 1.5'' plastic resealing bottle trap cover.

2.22   	Toilet Brush & Holder;

These shall be made of vitreous china conforming to BS 3402, & shall be white color.

It shall have overflow and one tap hole and shall come complete with single lever C.P. monobloc mixer with pop-up waste with ceramic disc cartridge and with 28 mm C.P. water, bottle trap and C.P. tail and flange at wall (panel) entry.

2.23   	Tap & Hand Spray;

Shall comprise in dia. CP inclined bib top complete with flexible CP hose, jet and wall hook.

# PART 3       EXECUTIONS

3.1   	INSTALLATION

Listing of Product Installation shall be submitted for plumbing fixtures identifying at least five units, similar to those proposed for use, that have been in successful service for a minimum of five years.  The list shall include purchaser, address of installation, service organization, and date of installation.

Materials, equipment, and fixtures shall be installed as indicated and specified and in accordance with the manufacturer's recommendations.

Installation of plumbing fixtures shall conform to the published or written instructions of the manufacturer for the specific project application, except as otherwise specified herein.

Fixtures shall be clean and free of deleterious material before being installed.  Before connecting to water, waste, vent or trap service, the fixture lines shall be blown out with compressed air.  During the progress of construction, open ends of fixtures shall be protected at all times to prevent the admission of foreign matter.

All hand sprays shall be installed with isolating valve and certified backflow preventer.

Where vacuum flow is likely to occur, due to water circulation or any other reason, vacuum breakers shall be provided

3.2   	TESTS

Tests shall be hydrostatic, unless otherwise specified.  Only potable water shall be used for testing. The Employer will supply the test water, but the Contractor shall be responsible for approved disposal of contaminated water.

Duration of the test will be determined by the Engineer, who may also terminate the test at any point after it has been determined that fixtures are watertight.

Record of testing shall be maintained by the Contractor and shall be submitted to the Engineer upon acceptance of the equipment by the Employer.

3.3 	OPERATIONS AND MAINTENANCE

Contractor shall submit 6 copies of the Operation and Maintenance Manuals 30 days prior to testing of plumbing fixtures.  Data shall be updated and resubmitted for final approval no later than 30 days prior to contract completion.

End Of Section

Section 16

Testing & Commissioning Specifications
Table of Contents

| 1.1 | Testing and Commissioning | 416 |
| --- | --- | --- |
| 1.1.1 | General | 416 |
| 1.1.2 | Notice Prior to Testing | 416 |
| 1.1.3 | Testing in Sections | 416 |
| 1.1.4 | Compliance Tests | 416 |
| 1.1.5 | Operating Tests | 416 |
| 1.1.6 | Off Site Tests | 417 |
| 1.1.7 | On Site Tests | 417 |
| 1.1.8 | Performance Tests | 418 |
| 1.1.9 | Acceptance Tests | 418 |
| 1.2 | Testing of Pipe work, Welds, Etc | 419 |
| 1.3 | Test Certificates | 420 |
| 1.4 | Air and Hydraulic Systems Testing, Balancing & Commissioning | 421 |
| 1.4.1 | Scope | 421 |
| 1.4.2 | Related Work under Mechanical Sections | 421 |
| 1.4.3 | Guarantees | 421 |
| 1.4.4 | Commissioning Agency | 421 |
| 1.4.5 | Standards | 422 |
| 1.4.6 | Tests | 422 |
| 1.4.7 | Notice | 422 |
| 1.4.8 | Submittals | 422 |
| 1.4.9 | Instruments | 423 |
| 1.4.10 | General Requirements | 425 |
| 1.5 | Commissioning | 432 |
| 1.5.1 | Testing and Commissioning of Controls, MCC's | 433 |
| 1.5.2 | Commissioning records | 435 |
| 1.5.3 | Performance Tests | 437 |
| 1.5.4 | Equipment Cards | 438 |
| 1.5.5 | Documentation | 438 |

  - Testing and Commissioning

1.1.1 General

Systems and components shall be tested during construction in accordance with the requirements of the relevant clauses of the documents. Adequate time shall be allowed for the stair pressurization and smoke exhaust systems to be fully tested and commissioned correctly

The Engineer shall witness all testing and commissioning and shall have access at all reasonable times to such parts of the Contractor's and Contractors' works as may be necessary for the purpose of inspecting, examining and testing the materials, workmanship and performance.

1.1.2 Notice Prior to Testing

The Contractor shall give the Engineer seven days' written notice of his intention to carry out a test and shall have carried out all necessary adjustment prior to commencing the test.

1.1.3 Testing in Sections

The Contractor shall allow for testing and commissioning the installation in sections as may be required in order to conform to the program. All pipe work and ductwork in these sections shall be sealed and tested as specified below, so that the insulation can be applied and the section completed to assist the program.

1.1.4 Compliance Tests

Certificates showing compliance with the requirements of these documents and of any authority having jurisdiction shall be furnished.

1.1.5 Operating Tests

Operating tests shall be carried out prior to Practical Completion and a detailed report shall be furnished at completion showing the preliminary readings and final balance figures for each circulating system, name plate rating and full load operating current for each motor, the settings for each electrical and control element.

Balancing is to be by NATA, BSRIA accredited organization or by NEBBO tested personnel with specialized expertise in air and water balancing.

1.1.6 Off Site Tests

When called for by the Authorized Representative or where British Standards or Codes of Practice stipulate tests on items of equipment to demonstrate compliance, these tests shall be carried out at the manufacturer's works or elsewhere, as appropriate. In certain cases, where appropriate, type test certificates will be accepted as follows:

a) Fans: Type Test Certificates showing fan characteristic curves, (BS 848, Part 1, test method as appropriate) and Type Test Certificates for sound power levels (BS 848, Part 2).

b) Pumps: Type Test Certificates for head, discharge, speed and power input (BS 599)

c) Electric Motors: Type Test Certificates in accordance with BS 5000. For motors of 40 kW output and above, routine (individual) test certificates in accordance with BS 5000.

d) Starters and control gear: Type Test Certificates BS 587. For control panels as a whole routine (individual) high voltage test in accordance with BS 587.

e) Other electrical equipment, such as air heaters (but excluding thermostatic control equipment): Test Certificates in accordance with BS 6220.

f) Refrigeration and A/C plant: Test Certificates for hydraulic and air pressure testing at works in accordance with BS 4434, Part 1.

1.1.7 On Site Tests

Carry out pressure tests on all ductwork and piping systems in accordance with the requirements of this specification, relevant clauses: Air Systems Adjustments shall be made at each air terminal to provide an even distribution over the face. Air quantity shall be balanced to within +10 0% of the value shown on the drawings with volume dampers set to achieve the lowest practical fan speed and power consumption. Blade pitch and fan speed setting to deliver +10% 0% of the design value shall adjust fan air quantity. Air quantity at pilot traverse stations shall be measured and recorded. In each system the sum of the individual terminal air quantities shall be within +5% 5% of the upstream pilot traverse quantity. Fan speed and pitch shall be recorded. Controls Pressure, temperature and humidity controllers shall be tested and adjusted to operate at the correct settings. Pressure and temperature limit controls shall be tested and adjusted to safe operating settings and trip times. Interlocked and multi-step systems shall be tested for operating sequence. Thermal overloads and protective cut outs shall be tested and adjusted during a hot day for the operating load. Generally Cooling equipment shall be tested for satisfactory operation. Pressures and temperatures for refrigerant and cooling water shall be tested and adjusted to the correct operating settings. Any abnormalities in terms of vibration and noise shall be corrected. Unusual operation in rotating machinery shall be corrected by testing for alignment and support. Noisy air terminals shall be corrected by rebalancing.

1.1.8 Performance Tests

A detailed report shall be furnished at the completion of performance tests.
Air Cooling Systems
Cooling tests shall be conducted in summer climatic conditions.

Measuring air total heat difference and refrigerant temperatures simultaneously at the balanced flow rates shall test the capacity of each cooling coil.

Refrigeration compressor capacity shall be read from manufacturer's rating information using measured suction and discharge pressures and operating current step by step.

Controls

Operating pressures, temperatures and humidity’s shall be tested under operating conditions. The set point and differential operating range of each control element shall be recorded. The recorded readings shall be entered on the "As Built" control drawing. (See "Instruction Manuals").

Three copies of recorded data for final system set up shall be forwarded to the Project Manager after final acceptance tests.

1.1.9 Acceptance Tests

At the beginning of the Defects Liability period acceptance tests shall be conducted to demonstrate that systems and components are performing in accordance with the requirements.

Final acceptance testing of control systems shall be conducted in the presence of a representative of the Main Contractor. During testing, the control characteristics, interlocks, and responses of all relevant control systems shall be demonstrated to the satisfaction of the Main Contractor. Witnessed testing shall not be arranged until the Mechanical Contractor has assured himself that all systems are functioning correctly and are capable of maintaining reliable and consistent operation.

The acceptance tests shall include a period of two days operation of control systems during which time the performance of the systems shall be carefully observed and important parameters logged or recorded. Where possible, the plants shall be operated under extreme conditions of service by artificially loading if necessary.

Logging and Documentation

During the commissioning and testing period, the settings of all control elements shall be logged and documented for inclusion in Operation and Maintenance Manuals. The logs shall provide a complete record of commissioning data for the plant including final settings, special adjustments or requirements, and other useful data such as recorder charts etc. Three (3) copies of commissioning logs shall be forwarded to the Main Contractor after final acceptance tests.

Where results are inconclusive tests shall be repeated.

If the second test should fail all further witnessing of tests by the Main Contractor or his representative shall be chargeable at his currently hourly rate and the accumulated sum shall be deducted from the amounts payable under the Contract.

1.2 Testing of Pipe work, Welds, Etc.

The whole installation shall be hydraulically tested to twice the working pressure of the systems or 4.137 bar, whichever is the greater.

Gas pipe work shall be tested as above, but utilizing an inert gas.

The pressure shall be maintained for a period of two hours in each case, and due allowance shall be made for attendance by the Engineer during the progress of such tests. The Contractor shall also be responsible for arranging for the water authority to witness this test should they require to do so. Any equipment fitted not suitable for this pressure shall be adequately protected or isolated from the system during the test.

All leaks are to be immediately repaired and the installations retested until the above requirements are obtained.

The Contractor shall allow for such emptying and refilling and maintenance until all leaks have been satisfactorily stopped.

Upon completion of the final hydraulic test on the system, the Contractor shall apply heat and open all valves and charge the calorifiers.

All valves and stopcocks throughout the system shall be adjusted and regulated until all circuits are working under normal conditions and to the satisfaction of the Engineer. Joints found to be faulty under heat are to be completely remade.

All tests are to be carried out before application of the paint or insulation and valve adjustments made with the circulating pumps in operation.

The Contractor shall ensure that before informing the Engineer of the proposed tests, all remedial work has been carried out and that there are no leaks. Failure to comply with this Clause could result in a charge being made by the Engineer to the Contractor for the abortive visit.

Each welder shall be assigned a reference, which shall be stamped on each weld and when the general hydraulic tests of the completed systems are carried out, each weld shall be lightly hammered during the time that pressure is maintained.

If any leaks occur at welds, the portion of the weld near the leak shall be cut out and re welded. Such leaks shall not be repaired by caulking or attempted fusion of the surrounding metal. Should a considerable portion of the welded joints made by a particular operator be found to be defective due to faulty workmanship, all such welds shall be cut out and re welded by another -operator, whose work has proved satisfactory.

During the progress of the Works, inspection will be made by the Engineer to ensure that all burrs and swarf have been removed from cuts and that the cuts have been made square.

The Engineer reserves the right to instruct the Contractor to cut open any sections of the pipe work to inspect cuts or to have welded joints laboratory tests.

If the test and inspection should prove that the welds are to the required standard or that all burrs and swarf have been removed, the Client will pay costs incurred by the Contractor in removing testing and replacing the Sections of pipe work. If, however, the inspection and test show that the welds or cuts are below the class of workmanship for this class of work, or if they are found to be faulty in any respect, the Contractor shall make good any such faults free of cost to the Client and shall pay all fees incurred by the tests.

If, in the opinion of the Engineer, this result suggests that the standard of workmanship on the whole of the rest of the work is below that required, the Engineer shall be entitled to instruct the Contractor to remove the remainder of the sections in whole or in part and have these sections renewed to conform with this Specification. The Contractor in this case shall have no claim for the costs involved in removing and renewing these sections of the works, whether such Works are found to be faulty or not.

The Engineer's decision shall be final.

1.3 Test Certificates

The Contractor shall at the time of the test present copies of a test certificate for signature by the Engineer and one to be retained by the Contractor.

Insurance company certificates of hydraulic test held at the Manufacturer's work shall be submitted for boilers calorifiers, cylinders.

Manufacturers' certificates, of test at the specified duties held at the manufacturers' works shall be submitted for pumps and fans. No item of equipment shall be delivered to Site before the Engineer has given his approval of the test certificate. Where no test pressures at factory are given, the test shall be carried out on Site in accordance with the appropriate British Standard (current edition) and subject to the Engineer's approval.

1.4 Air and Hydraulic Systems Testing, Balancing & Commissioning

1.4.1 Scope

Inspect, test, commission and monitor all mechanical services systems and equipment included in this contract together with associated control systems and panels.

Provide all personnel and equipment necessary to carry out the required inspections, tests and commissioning operations including the employment of specialists who would provide and operate testing and monitoring facilities.

1.4.2 Related Work under Mechanical Sections

This section shall relate to all sections included in this contract.

1.4.3 Guarantees

Attention is directed to provisions of the General Terms and Conditions and Special Conditions regarding guarantees and warranties for work under this contract.

1.4.4 Commissioning Agency

The HVAC and Mechanical contractor shall employ the services of a company approved by the Engineer regularly engaged in providing a testing and commissioning service and who has been in continuous business for not less than 5 years employing fully trained staff having not less than 2 years dedicated experience. A senior experienced commissioning technician shall be responsible for supervising and directing the activities of the commissioning team.

A fully commissioning team shall be provided throughout the full period of commissioning. Changes to the staffing of the commissioning team shall only be made at the request or approval of the Authorized Representative.

The company shall have no vested interest in Project, such as sales of equipment, services etc. and shall not be partly or wholly an owned subsidiary of any vested or interested party, contractor or sub-contractor.

1.4.5 Standards

All inspection, testing and commissioning procedures shall conform to the current editions and amendments thereto of the following standards and codes not withstanding current statutory and legal requirements and any other standards and codes which shall apply.

C.I.B.S. Commissioning Codes;

Series A -Air Distribution
Series B -Boiler Plant
Series C -Controls
Series R -Refrigerating Systems
Series W-Water Distribution systems

BSRIA Application guides and Technical Notes

D.W. 142 Specifications
British standards and Codes of Practice

I.E.E. Regulations
Local Authority Regulations and Bye-Laws
Health and Safety at Work Act
Government Regulations
Insurance Company(s) Requirements

1.4.6 Tests

All tests shall be witnessed and test certificates signed by the Authorized Representative upon satisfactory completion of the tests. One copy of the signed certificate shall be immediately handed to the Authorized Representative.

1.4.7 Notice

Clear notice required by the Authorized representative of testing and commissioning activities.

Off site tests : 14 days
On site tests and inspection : 2 days
Start up of major plant : 7 days
Performance tests : 14 days

1.4.8 Submittals

Four (4 No.) copies of all testing and commissioning documentation shall be submitted in bound covers indicated as follows:

A. Certificates:

- 1.	Equipment test certificates

- 2.	System(s) test certificates

- 3.	Welding test certificates if applicable

B. Data Sheets and record manuals:

- 1.	Data sheets of test equipment to be used.

- 2.	Full commissioning and testing data presented on approved record forms for all systems and equipment.

C. Drawings:

- 1. Equipment detail drawings for equipment.

- 2.	Circuit diagrams for each system with design and actual flow rates and other pertinent data shown.

D. Record forms:

1 Specimen copies of all commissioning record forms shall be submitted for approval of their use on this project.

2	Forms shall be A4 size paper for loose leaf binding, with blanks for listing of the required test ratings and for certification of report.

E. Program of work:

Fully detailed program of work for inspecting, testing and commissioning the works, shall be submitted for approval.

1.4.9 Instruments

i)	All necessary instruments for commissioning and testing as defined in the C.I.B.S.E codes and this specification shall be included.

ii)	All instruments shall have been calibrated within a period of six months and carry a certificate of calibration to that effect. The instruments shall be selected to provide an accuracy compatible with the readings to be taken and the tolerances specified.

iii)	The accuracy of the instruments shall be demonstrated to the Authorized Representative and the use thereof shall be subject to his approval.

B.	Test instruments shall be available for use to obtain the readings and recorded data required, and shall include but not be limited to the following:-

  - 1.	Temperature and humidifies:

  - a) Electronic thermometers
b) Mercury in glass thermometers
c) Aspirated/sling hygrometers
2.	Pressures:

a) Manometer gauges
b) Magnehelic gauges (diaphragm actuated)
c) Pressure gauges
d) Test pressuring equipment

3. Air flow:

a) Pitot static gauges
b) Hot wire anemometers
c) Vane anemometer (analogue or digital) with hoods
d) Velometers (grilles and diffusers only)

4. Liquid Flow

a) Manometer gauges across venturies, orifice plates, valves or equipment.
b) Anuber (Pitot) gauges
c) Flow meters

d) Portable pumps

  - 5. Air Movements

  - a) Smoke pellets
b) Smoke aspirator

  - 6. Rotational Speeds:

  - a) Direct read out electronic digital tachometer
b) Revolution counter and stop watch

- 7. Sound Levels:
a) Sound spectrum analyzer

  - 8. Electrical:

  - a) Ammeters
b) Voltmeters
c) Multi-meters

- 9.	Vibration:
a) Accelerometer

- 10. Recording Instruments:

a) Hydro thermograph
b) Multi-point temperature/humidity recorder (plotter)
c) Digital pressure recorder (plotter)
d) Sound level recorder

1.4.10 General Requirements

A) Definitions:

- 1.	Commissioning: The advancement of the installation from the static completion to full working order calibrated to design requirements, involving the setting-to-work and regulation of the installation (s).

- 2.	Testing: The evaluation of the performance of the commissioned works.

NB:	Preliminary checks on the static installation will carried out by the commissioning Engineers to ensure that it is in a satisfactory and safe condition immediately prior to start up.

B)	The Contractor shall apply for, obtain and pay for all permits, tests and inspections that may be required by any of the authorities or agencies having jurisdiction in the performance of the work.

C)	Under the adjudication of the Authorized Representative, the Contractor shall coordinate, supervise and carry out all inspection, testing and commissioning activities within an agreed program period.

D)	The Contractor shall prepare, submit and agree with the Authorized Representative a detailed program of work defining for each stage: activities, sequence of work, time scales, manpower requirements, start and completion dates and working areas of the building to which access will be required.

E)	The Contractor shall allow for carrying out testing and commissioning of the works in phases/stages.

F)	The Contractor shall allow for carrying out activities in an occupied building with premium working out of normal office hours in the evening and at weekends.

G)	All defects of workmanship, materials, performance design of equipment, maladjustment's or other irregularities, which become apparent during tests, shall be rectified and the tests repeated to the Authorized Representative's satisfaction and at no cost to the contract.

H)	Where equipment requires inspection or certification by an insurance company during construction adequate notification shall be given of the date when the equipment will be ready for examination. This shall also apply to on site tests to be witnessed by an insurance company.

I)	Before any electrical circuit is energized an "Application for Supply" shall be made. This shall be delivered 24 hours before the supply is required and shall be accompanied by a Test Certificate showing the witnessed values of insulation, resistance and earth fault loop impedance

obtained.

J) Before any installation is subjected to site testing or commissioning it shall be thoroughly cleaned both internally and externally.

Where fire protection systems are installed they shall be installed in stages to suit the program of work, but upon construction of the first 18 meters in height they shall be capped off at this height and hydrostatically tested. this section of the riser shall then be made operative to provide protection to the building. This procedure shall be repeated floor by floor thereafter until the system has been completed after which the entire installation shall be re-tested. AIR SYSTEMS' BALANCING PROCEDURES

A.	Prepare test reports for both fans and outlets. Obtain manufacturer's outlet factors and recommended testing procedures. Crosscheck the summation of required outlet volumes with required fan volumes.

B.	Prepare schematic diagrams of systems' "as-built" duct layouts.

C.	For variable-air-volume systems, develop a plan to simulate diversity.

D.	Determine the best locations in main and branch ducts for accurate duct airflow measurements.

E.	Check the airflow patterns from the outside-air louvers and dampers and the return-and exhaust-air dampers, through the supply-fan discharge and mixing dampers.

F.	Locate start-stop and disconnect switches, electrical interlocks, and motor starters.

G.	Verify that motor starters are equipped with properly sized thermal protection.

H.	Check dampers for proper position to achieve desired airflow path.

I.	Check for airflow blockages.

J.	Check condensate drains for proper connections and functioning.

K.	Check for proper sealing of air-handling unit components.

  - 3.5 CONSTANT-VOLUME AIR SYSTEMS' BALANCING PROCEDURES

  - A.	The procedures in this Article apply to constant-volume supply-, return-, and exhaust-air systems.

  - B.	Adjust fans to deliver total design airflows within the maximum allowable rpm listed by the fan
manufacturer.

  - 1.	Measure fan static pressures to determine actual static pressure as follows:

  - a.	Measure outlet static pressure as far downstream from the fan as practicable and upstream from restrictions in ducts such as elbows and transitions.

  - b.	Measure static pressure directly at the fan outlet or through the flexible connection.

  - c.	Measure inlet static pressure of single-inlet fans in the inlet duct as near the fan as possible, upstream from flexible connection and downstream from duct restrictions.

  - d.	Measure inlet static pressure of double-inlet fans through the wall of the plenum that houses the fan.

  - 2.	Measure static pressure across each air-handling unit component.

  - a.	Simulate dirty filter operation and record the point at which maintenance personnel must change filters.

    - 3.	Measure static pressures entering and leaving other devices such as sound traps, heat recovery equipment, and air washers under final balanced conditions.

    - 4.	Compare design data with installed conditions to determine variations in design static pressures versus actual static pressures. Compare actual system effect factors with calculated system effect factors to identify where variations occur. Recommend corrective action to align design and actual conditions.

    - 5.	Adjust fan speed higher or lower than design with the approval of the Engineer. Make required adjustments to pulley sizes, motor sizes, and electrical connections to accommodate fan-speed changes.

    - 6.	Do not make fan-speed adjustments that result in motor overload. Consult equipment manufacturers about fan-speed safety factors. Modulate dampers and measure fan-motor amperage to ensure no overload will occur. Measure amperage in full cooling, full heating, and economizer modes (if applicable) to determine the maximum required brake horsepower.

  - C.	Adjust volume dampers for main duct, submain ducts, and major branch ducts to design airflows within specified tolerances.

  - 1.	Measure static pressure at a point downstream from the balancing damper and adjust volume dampers until the proper static pressure is achieved.

  - a.	Where sufficient space in submains and branch ducts is unavailable for Pitot-tube traverse measurements, measure airflow at terminal outlets and inlets and calculate the total airflow for that zone.

  - 2.	Remeasure each submain and branch duct after all have been adjusted. Continue to adjust submains and branch ducts to design airflows within specified tolerances.

  - D.	Measure terminal outlets and inlets without making adjustments.

  - 1.	Measure terminal outlets using a direct-reading hood or the outlet manufacturer's written instructions and calculating factors.

  - E.	Adjust terminal outlets and inlets for each space to design airflows within specified tolerances of design values. Make adjustments using volume dampers rather than extractors and the dampers at the air terminals.

    - 1.	Adjust each outlet in the same room or space to within specified tolerances of design quantities without generating noise levels above the limitations prescribed by the Contract Documents.

    - 2.	Adjust patterns of adjustable outlets for proper distribution without drafts.

- 3.6 VARIABLE-AIR-VOLUME SYSTEMS' ADDITIONAL PROCEDURES

A.	Compensating for Diversity: When the total airflow of all terminal units is more than the fan design airflow volume, place a selected number of terminal units at a maximum set-point airflow condition until the total airflow of the terminal units equals the design airflow of the fan. Select the reduced airflow terminal units so they are distributed evenly among the branch ducts.

B.	Pressure-Independent, Variable-Air-Volume Systems: After the fan systems have been adjusted, adjust the variable-air-volume systems as follows:

- 1.	Set outside-air dampers at minimum, and return-and exhaust-air dampers at a position that simulates full-cooling load.

- 2.	Select the terminal unit that is most critical to the supply-fan airflow and static pressure. Measure static pressure. Adjust system static pressure so the entering static pressure for the critical terminal unit is not less than the sum of the terminal unit manufacturer's recommended minimum inlet static pressure plus the static pressure needed to overcome terminal-unit discharge duct losses.

- 3.	Measure total system airflow. Adjust to within 10 percent of design airflow.

- 4.	Set terminal units at maximum airflow and adjust controller or regulator to deliver the designed maximum airflow. Use the terminal unit manufacturer's written instructions to make this adjustment. When total airflow is correct, balance the air outlets downstream from terminal units as described for constant-volume air systems.

- 5.	Set terminal units at minimum airflow and adjust controller or regulator to deliver the designed minimum airflow. Check air outlets for a proportional reduction in airflow as described for constant-volume air systems.

a.	If air outlets are out of balance at minimum airflow, report the condition but leave the outlets balanced for maximum airflow.

- 6.	Remeasure the return airflow to the fan while operating at maximum return airflow and minimum outside airflow. Adjust the fan and balance the return-air ducts and inlets as described for constant-volume air systems.

- 7.	Measure static pressure at the most critical terminal unit and adjust the static-pressure controller at the main supply-air sensing station to ensure adequate static pressure is maintained at the most critical unit.

- 8.	Record the final fan performance data.

C.	Pressure-Dependent, Variable-Air-Volume Systems with Diversity: After the fan systems have been adjusted, adjust the variable-air-volume systems as follows:

- 1.	Set system at maximum design airflow by setting the required number of terminal units at minimum airflow. Select the reduced airflow terminal units so they are distributed evenly among the branch ducts.

- 2.	Adjust supply fan to maximum design airflow with the variable-airflow controller set at maximum airflow.

- 3.	Set terminal units being tested at full-airflow condition.

- 4.	Adjust terminal units starting at the supply-fan end of the system and continuing progressively to the end of the system. Adjust inlet dampers of each terminal unit to design airflow. When total airflow is correct, balance the air outlets downstream from terminal units as described for constant-volume air systems.

- 5.	Adjust terminal units for minimum airflow.

- 6.	Measure static pressure at the sensor.

- 7.	Measure the return airflow to the fan while operating at maximum return airflow and minimum outside airflow. Adjust the fan and balance the return-air ducts and inlets as described for constant-volume air systems.

3.7 FUNDAMENTAL PROCEDURES FOR HYDRONIC SYSTEMS

A.	Prepare test reports with pertinent design data and number in sequence starting at pump to end of system. Check the sum of branch-circuit flows against approved pump flow rate. Correct variations that exceed plus or minus 5 percent.

B.	Prepare schematic diagrams of systems' "as-built" piping layouts.

C.	Prepare hydronic systems for testing and balancing according to the following, in addition to the general preparation procedures specified above:

- 1.	Open all manual valves for maximum flow.

- 2.	Check expansion tank liquid level.

- 3.	Check makeup-water-station pressure gage for adequate pressure for highest vent.

- 4.	Check flow-control valves for specified sequence of operation and set at design flow.

- 5.	Set differential-pressure control valves at the specified differential pressure. Do not set at fully closed position when pump is positive-displacement type, unless several terminal valves are kept open.

- 6.	Set system controls so automatic valves are wide open to heat exchangers.

- 7.	Check pump-motor load. If motor is overloaded, throttle main flow-balancing device so motor nameplate rating is not exceeded.

- 8.	Check air vents for a forceful liquid flow exiting from vents when manually operated.

3.8 HYDRONIC SYSTEMS' BALANCING PROCEDURES

A.	Determine water flow at pumps. Use the following procedures, except for positive-displacement pumps:

- 1.	Verify impeller size by operating the pump with the discharge valve closed. Verify with the pump manufacturer that this will not damage pump. Read pressure differential across the pump. Convert pressure to head and correct for differences in gage heights. Note the point on the manufacturer's pump curve at zero flow and confirm that the pump has the intended impeller size.

- 2.	Check system resistance. With all valves open, read pressure differential across the pump and mark the pump manufacturer's head-capacity curve. Adjust pump discharge valve until design water flow is achieved.

- 3.	Verify pump-motor brake horsepower. Calculate the intended brake horsepower for the system based on the pump manufacturer's performance data. Compare calculated brake horsepower with nameplate data on the pump motor. Report conditions where actual amperage exceeds motor nameplate amperage.

- 4.	Report flow rates that are not within plus or minus 5 percent of design.

B.	Set calibrated balancing valves, if installed, at calculated presettings.

C.	Measure flow at all stations and adjust, where necessary, to obtain first balance.

1.	System components that have Cv rating or an accurately cataloged flow-pressure-drop relationship may be used as a flow-indicating device.

D.	Measure flow at main balancing station and set main balancing device to achieve flow that is 5 percent greater than design flow.

E.	Adjust balancing stations to within specified tolerances of design flow rate as follow:

- 1.	Determine the balancing station with the highest percentage over design flow.

- 2.	Adjust each station in turn, beginning with the station with the highest percentage over design flow and proceeding to the station with the lowest percentage over design flow.

- 3.	Record settings and mark balancing devices.

F.	Measure pump flow rate and make final measurements of pump amperage, voltage, rpm, pump heads, and systems' pressures and temperatures, including outdoor-air temperature.

G.	Measure the differential-pressure control valve settings existing at the conclusions of balancing.

3.9 VARIABLE-FLOW HYDRONIC SYSTEMS' ADDITIONAL PROCEDURES

A.	Balance systems with automatic 2-and 3-way control valves by setting systems at maximum flow through heat-exchange terminals and proceed as specified above for hydronic systems.

3.10 PRIMARY-SECONDARY-FLOW HYDRONIC SYSTEMS' ADDITIONAL PROCEDURES

A.	Balance the primary system crossover flow first, then balance the secondary system.

3.11 MOTORS

A.	Motors, 1/2 HP and Larger: Test at final balanced conditions and record the following data:

- 1.	Manufacturer, model, and serial numbers.

- 2.	Motor horsepower rating.

- 3.	Motor rpm.

- 4.	Efficiency rating if high-efficiency motor.

- 5.	Nameplate and measured voltage, each phase.

- 6.	Nameplate and measured amperage, each phase.

- 7.	Starter thermal-protection-element rating.

B.	Motors Driven by Variable-Frequency Controllers: Test for proper operation at speeds varying from minimum to maximum. Test the manual bypass for the controller to prove proper operation. Record observations, including controller manufacturer, model and serial numbers, and nameplate data.

3.12 HEAT-TRANSFER COILS

A.	Water Coils: Measure the following data for each coil:

- 1.	Entering-and leaving-water temperatures.

- 2.	Water flow rate.

- 3.	Water pressure drop.

- 4.	Dry-bulb temperatures of entering and leaving air.

- 5.	Wet-bulb temperatures of entering and leaving air for cooling coils designed for less than 3540 L/s.

- 6.	Airflow.

- 7.	Air pressure drop.

B.	Electric-Heating Coils: Measure the following data for each coil:

- 1.	Nameplate data.

- 2.	Airflow.

- 3.	Entering-and leaving-air temperatures at full load.

- 4.	Voltage and amperage input of each phase at full load and at each incremental stage.

- 5.	Calculated kW at full load.

- 6.	Fuse or circuit-breaker rating for overload protection.

3.13 TEMPERATURE TESTING

A.	During testing, adjusting, and balancing, report need for adjustment in temperature regulation within the automatic temperature-control system.

B.	Measure indoor wet-and dry-bulb temperatures every other hour for a period of 2 successive 8-hour days, in each separately controlled zone, to prove correctness of final temperature settings. Measure when the building or zone is occupied.

C.	Measure outside-air, wet-and dry-bulb temperatures.

  - 3.14 FUME HOODS

  - A.	Determine total airflow into the room where the fume hood is located and balance systems to ensure adequate air supply to all hoods.

    - 1.	Set fume-hood door opening at position of normal use.

    - 2.	Energize the exhaust fan and adjust airflow to provide the indicated average fume-hood face velocity at hood opening.

    - 3.	Measure exhaust airflow volume by measuring airflow by Pitot-tube duct traverse.

    - 4.	Measure air velocity using Pitot-tube traverse method.

    - 5.	Record each face velocity measurement taken at 100-to 150-mm increments over the entire hood door opening.

    - 6.	Calculate the average face velocity by averaging all velocity measurements.

    - 7.	Calculate the airflow volume of exhaust-hood face velocity by multiplying the calculated average face velocity by the opening area. Compare this quantity with exhaust volume at exhaust fan and report duct leakage.

    - 8.	Measure airflow volume supplied by makeup fan. Verify that the makeup system supplies the proper amount of air to keep the space at the indicated pressure with the exhaust systems in all operating conditions.

    - 9.	Retest for average face velocity. Adjust hood baffles, fan drives, and other parts of the system to provide the indicated average face velocity and the indicated auxiliary air-supply percentages.

    - 10.	Retest and adjust the systems until fume-hood performance complies with Contract Documents.

- 3.15 TEMPERATURE-CONTROL VERIFICATION

A.	Verify that controllers are calibrated and commissioned.

B.	Check transmitter and controller locations and note conditions that would adversely affect control
functions.

C.	Record controller settings and note variances between set points and actual measurements.

D.	Verify operation of limiting controllers (i.e., high-and low-temperature controllers).

E.	Verify free travel and proper operation of control devices such as damper and valve operators.

F.	Verify sequence of operation of control devices. Note air pressures and device positions and correlate with airflow and water-flow measurements. Note the speed of response to input changes.

G.	Confirm interaction of electrically operated switch transducers.

H.	Confirm interaction of interlock and lockout systems.

I.	Verify main control supply-air pressure and observe compressor and dryer operations.

J.	Record voltages of power supply and controller output. Determine if the system operates on a grounded or non grounded power supply.

1.5 Commissioning

Checks and Procedures

A)	Prior to any work being commenced, a thorough inspection of all systems, plant and equipment shall be carried out to check for installation errors, damage, deterioration cleanliness and readiness for testing and commissioning. all defects shall be recorded in detail, which shall be rectified before work can proceed.

B)	When the above procedure has been satisfactorily completed the sequence for each main system shall comprise:

i) Mechanical and electrical engineering safety checks. ii) Start up and run machines. Pumps shall not be run until system flushing is complete unless used for dynamic flushing. iii) Regulation calibration or adjustment.

C)	The preferred sequence for commissioning the system is :

i)	Flushing and pre commissioning cleaning only of water systems.

ii)	Commissioning of air distribution systems.

iii)	Filling, venting, water treatment, start up and regulation of water systems.

iv)	Functional checks on thermal controls associated with water distribution.

v)	Commissioning of boiler and calorifier plants and associated controls.

vi) Commissioning of air conditioning and refrigeration plants including associated controls. vii) Commissioning of controls for air conditioning and ventilation plant. viii) Commissioning of fire and other safety control circuits including instrumentation,

sensing and remote indication.

D)	The precise sequence may have to be adjusted for readiness of plant and suitability of weather conditions, subject to the prior approval of the Authorized Representative.

E)	All water systems, air distribution systems, plant and equipment and control systems shall be

fully commissioned in accordance with the C.I.B.S. Commissioning Codes and this

Specification.

Where connections to existing services are required, the existing services shall be thoroughly checked and tested also cleaned and repaired where necessary before connecting into new systems.

The tolerance for adjustment of air flow rates shall be generally as stated in C.I.B.S. Commissioning Codes but subject to agreement with the Authorized Representative. Water flow rates shall be adjusted such that volumes to each branch shall be ± 10% of design values and pump volumes shall be + 10%, -10% of the design value.

The detailed procedure for preliminary checks, setting to work and regulation of the works shall be carried out strictly in accordance with the relevant C.I.B.S. code(s). No deviations to these procedures shall be made without the prior written approval of the Authorized Representative.

Commissioning shall not be considered as complete until the Authorized Representative's approval has been obtained.

During the commissioning period of controls arrange for a controls systems engineer to be available on site until the controls systems have been fully commissioned and the witnessing of proving tests have been carried out.

Particular attention shall be paid to the following features:

- •	Satisfactory operation of any automatic of manually operated sequences to be used in the event of fire.

- •	Safety in the event of failure and of sudden resumption of electricity supply.

- •	Satisfactory operation of safety interlocks designed for the protection of personnel, such as those associated with the high voltage side of equipment and with remote electrically operated plant. The following item shall checked and/or tested:

- •	Set desired value of all control devices.

- •	Satisfactory operation of equipment protection devices.

- •	The functional correctness of all on/off sequencing interlocks, operations and alternate working selections, automatic or manual change-over of duplicate plant, and modulation ability of all control systems.

The satisfactory operation of all make-up, drain and overflow arrangements shall be checked. Where water treatment is included initial commissioning shall be carried out and then rates of flow, dosing quantities etc. shall be calibrated and set for routine operation. where controlled blow down is included the controlling device shall be calibrated and set for routine operation.

Damper setting positions shall be scribed on completion of air system balancing.

1.5.1 Testing and Commissioning of Controls, MCC's

a. General

All control panels and motor control centers when specified shall be pre-tested at works prior to delivery.

Where it is necessary for the Architect or his Representatives to visit places away from the Works for supervision or inspection in compliance with the Contract, the Contractor shall pay the traveling, subsistence and accommodation expenses of the Architect and his Representation.

Commissioning shall be carried out in accordance with theses requirements together with the

C.I.B.C.S. Commissioning Code 'C' and relevant I.E.E. Codes and British Standards for testing equipment.

The commissioning shall be completed within the time scales laid down by the Authorized Representative of the Engineer.

The Tender shall include for the provision of all equipment and apparatus necessary for carrying out commissioning and testing on site and to certify that the specified commissioning procedures have been carried out.

b. Static Checks

Checks shall be carried out on all control components to ensure proper location and installation.
All anomalies shall be corrected.
Checks shall be carried out to ensure that all control circuit wiring is complete and is safely and
correctly installed.

Checks shall be carried out on circuit continuity and earth leakage.

Visual inspection shall be made of all associated motors and equipment to ensure conditions are safe prior to start-up and running.

Checks shall be carried out on rating of all fuses and overloads, and on settings of all safety devices to design requirements.

c. Commissioning

All control systems shall be progressed from the completion of the static installation to full working order, calibrated to design requirements.

d. Testing

All control systems shall be fully tested to check:

) Functional correctness
) Modulating ability
) Sequence operation and interlocks
) Operation of safety circuits and devices
) Control ability within design limits

All information relating to controls including temperatures, etc. The information shall be maintenance and operation instructions.

set points, control bands limits, pressures, logged for tabulation and inclusion in the

Fault and limit conditions shall be simulated to ensure correct response occurs.

Performance tests shall be carried out to demonstrate that the control systems operate safely and correctly in accordance with the specification and are acceptable to the Authorized Representative of the Engineer.

e.	Inspections

Pre-Installation Inspection:

The area and conditions under which the control systems are to be installed shall be examined and any unsatisfactory conditions detrimental to the proper and timely completion of the work shall be corrected. The work shall not proceed until unsatisfactory conditions have been corrected in a manner suitable to the Authorized Representative of the Engineer.

f. Post-Installation Check:

The services of an experienced and competent Engineer/Technician of the manufacturer or contractor of the equipment shall be provided to visit site to inspect, check, adjust if necessary and approve the installations.

The equipment contractor's Engineer/Technician shall be present when equipment is placed in operation.

1.5.2 Commissioning records

- 1.	During the commissioning of the installation(s) the results of all checks and measurements taken for all systems and equipment shall be tabulated and recorded on approved record sheets. System and equipment design data shall also be tabulated on the same from for comparison.

- 2.	Written records are to be maintained, throughout the commissioning and testing, of all measurements made, and all settings and adjustment imposed on the plant. This shall include precise details of all thermal controls, including sensitivities, proportional bands, integral times and delay times. They shall be submitted to the Authorized Representative for approval as they are prepared at each stage of the works.

- 3.	All data shall be collated and produced as a single commissioning and testing record manual, enclosed in a loose leaf ringed plastic covered binder. On completion, a draft copy of the manual shall be submitted for approval prior to the production of the three final copies.

- 4.	The information recorded shall include but not necessarily be limited to the following, and shall also include all plant data including name of manufacturer, type of equipment, model number, system reference, etc.:

K. Note operation of electric actuators using spring return for proper fail-safe operations.

• Chillers:

Chilled water temps. at full load and through °C unloading range Chilled water flow on chiller L/S Chilled water pressure drop m/water Compressor/Motor power (name plate FLA) Amps Compressor/Absorbed elect. power at full load Amps Ambient Temp. °C Oil pressure/differential(s) bar Evaporating pressure(s) bar Condensing Pressure(s) bar High pressure cut-out setting bar Low pressure cut-out setting bar Low water temperature setting °C Oil pressure setting bar Loading and unloading system at partial and OK/Not full load OK Duty KWT

  - • Return and Extract Fans

  - Air flow L/S Total and static pressure mm Fan speed Rpm Fan power (absorbed) / phase Amp/Amp/Amp Motor speed Rpm Motor Power (name plate) FLA Amp

  - • Fan coil units

  - Air flow, supply and return L/S Air pressure drop across filter mm H20 On cooling coil air dry and wet bulb temps. °C Off cooling coil air dry and wet bulb temps. °C Water flow L/S Chilled water temperatures °C (at medium speed) Free field sound full spectrum dB Room Temp. (during maximum exposure to °C Sun) Vibration OK/Not OK Speeds of Motor OK/NOT OK

  - • Room Ventilation & Internal Temperatures

  - Supply air L/S Extract air L/S Main and sub-main duct L/S Internal Temperature °C Sound level dB(A)Hz

  - • Room Duct Heaters

  - Air flow L/S On heater air dry temperature °C Off heater air dry temperature 1st stage °C Off heater air dry temperature 2nd stage °C

- • Single package and split air conditioner

Supply air quantity L/S Return air quantity L/S Fresh air quantity L/S Total and static air pressures. (Indoor fan) mm H20 Evaporator fan speed Rpm Fan power (absorbed) / phase Amp/Amp/Amp Motor speed Rpm Motor power (name plate) FLA Amp Room internal temperature DB & WB °C Return air temperature °C Mixed air temperature °C Ambient dry bulb temperature °C Refrigerant suction pressure(s) bar Condensing pressure(s) bar Oil pressure differential pressure(s) bar High pressure cut-out setting bar Low pressure cut-out setting bar Duty Watt

Note

Single package units shall be tested and commissioned when relevant air compressors and vacuum pumps are operational.

  - • Pumping equipment

  - Water flow rate L/S static pressure m/water Suction pressure m/water Discharge pressure m/water Pump speed R.P.M. Pump power (absorbed)/phase Amp/Amp/Amp Motor speed R.P.M. Motor power (name plate) FLA Amp

- • Heat exchangers:

Primary water flow L/S Primary water on/off temps. °C Primary water pressure drop m/water

Secondary water flow L/S Secondary water on/off temps. °C Secondary water pressure drop m/water Duty Watt

  - • Water systems (piping & Control Valves)

  - Flow through main and sub-circuits L/S Flow through control valves L/S Pressure drop through control valves m/water Pressure drop across strainers m/water Supply temperature °C Return temperature (after coil) °C Return temperature (after mixing valve) °C

  - • Motor data:

  - Name plate power (FLA) Amp Voltage V Motor absorbed power/phase Amp/Amp/Amp Cycles Starting current Amp

- • Controls:

  - •	Expansion Tanks

    - H.P Operation	bar

    - H.P Switch setting	bar

    - L.P Operation	bar

    - L.P Switch Setting	bar

  - P.R.V. Switch Setting	bar

  - P.R.V. Setting bar Level in break tank mm. Float switch operation mm. Float switch setting mm.

  - •	Terminal Units

  - Damper motor operation
Interlock with hood and extract fan

  - •	Cold rooms and freezer rooms

  - Refrigerant Type Room temperature °C Ambient temperature on condenser °C Compressor suction pressure bar Compressor condensing pressure bar Sight glass indicator (full/partial) Compressor motor absorbed power Amp/Amp/Amp Compressor motor power rating FLA Amps Compressor motor applied voltage V Compressor motor rated voltage V

- •	Water treatment for A/C

|  | Set values of all control devices Control bands on all control devices Set values of all protection devices |  |
| --- | --- | --- |
| • | Vibration |  |
|  | Static deflection of mountings | mm. |
| • | Sound Levels: |  |
|  | (Free field sound full spectrum) | dB(A)Hz |
|  | Adjacent to :- |  |
|  | -Chillers and A/C Split and Packaged Units -Fans and air handling plant -Air intake and discharge louvers -Refrigeration condensing units |  |
| • | Steam boilers and calorifiers |  |
|  | Duty Steam Output Water "on" temp. (calorifiers) Water "off" temp (calorifiers) Water pressure drop (calorifiers) Control thermostat setting Safety thermostat setting | KW kgs/hr °C °C m/water °C °C |

Water (clean/dirty)
System passivation
Magmove separation

1.5.3 Performance Tests

- a.	Carry out and supervise the operation of the commissioned installations for such a period as necessary to satisfactorily evaluate and demonstrate to the authorized representative, the performance of the installations by use of measuring and recording instruments that the installations function correctly and maintain the required conditions within the specified limits.

- b.	Provide artificial loads as required for the purpose of simulating internal and external loads.

- c.	During the trial period, plant and building conditions shall be checked and monitored, all necessary adjustments made and recorded on final report sheets.

- d.	During the trial period, provide training to the clients nominated staff in the operation of the plant.

- e.	No test or trial shall be carried out while conditions are abnormal.

- f.	Provide the Authorized Representative with 14 days clear notice of proposed commencement

1.5.4 Equipment Cards

Install at each piece of equipment a "Check out" card showing all significant operating temperatures, pressures, amperes, voltages, power consumption flow rates, resistance, etc. Check out cards shall be standard 125 mm. x 200 mm. stiff index card enclosed in a clear film card folder, securely attached to equipment, or wall in immediate areas.

1.5.5 Documentation

The whole of the information requested in this specification including:-

- • plant data

- • test certificates

- • commissioning records

- • performance test reports

- • circuit diagrams

shall be collated, indexed and assembled into manuals having vinyl covered loose leaf ring binder covers with the project title and then words "Commissioning Data" permanently printed on the front cover. The commissioning companies name, address and telephone number shall be printed on the inside of the front cover.

Four sets of the above manuals shall be handed to the Authorized Representative within ten weeks of the completion of commissioning and performance tests. The installation shall not be accepted until the final approved manuals have been handed over.

SPECIFICATION

FOR THE ELECTRICAL WORK

CONTENTS

1.0General Equipment Requirements	440

1.1  Terminations	440

1.2Fixings	440

1.3Equipment Detail	440

2.0Labels And Notices	441

2.1  General	444

2.2Warning Notices	441

2.3Information Notices	441

2.4Distribution Board Labels	441

2.5Warning Labels	441

2.6Earthing System Warning Labels	442

3.0Testing And Inspection	442

3.1Distribution System	442

3.2Signal Cable	443

4. Power Cables	443

4.1 PVC and XLPE Insulated Power Cables	443

4.2 XLPE Insulated Power Cables	443

4.3 Finish	443

4.4 Standard Copper	443

4.5 Fillers	444

4.6 Bedding	444

4.7 Conductors-XLPE	444

4.8 Cable Specification	444

4.9 Conductors	444

4.10 Installation of PVC insulated Power Cables	444

4.11 Installation of Cables	444

4.12  Testing	445

4.13  Clearance	445

4.14   Bends	445

5.0Cables	445

5.1PVC Insulated Cables - Non Sheathed - Single Core	445

5.2PVC Insulated and Sheathed - Single and Multicore	445

5.3Joint in Conductors	445

5.4  General	445

5.5Cable Installation	446

ELECTRICAL WORKS

# 1.0	General Equipment Requirements

# 1.1  Terminations

The total of separate conductors and other circuit elements Conductors shall not be reduced at the termination in order to fit the terminal size. The terminal size shall be suitable for the size of cable being terminated.

# 1.2	Fixings

Each item shall include all fixings of his materials and necessary supports his equipments to complete the work as described in BOQ and any other documents.

The agreement of the Engineer shall be obtained for any fixing involving the cutting away of structural concrete or masonry walls.

The price of lighting items, Power socket items, switches, nurse call system, fire alarm system,  and Bed head units include all necessary junction boxes, wires, cables for BHU, labels, conduits, clamps, bolts, connectors and connecting all cables to switch boards.

# 1.3	Equipment Detail

Where the Contractor supplies an item of Plant or equipment which takes the form of a manufactured assembly of electrical and/or electronic components, he shall supply three sets of written information to the engineer, as follows:

Specification of each item of equipment showing:

- British or International Standard to which the equipment conforms

- Circuit diagram for each item of equipment

- Schedule of electronic or electrical components for each item of equipment with references to circuit diagram.

Details of equipment interconnection cables, sizes, number of cores and method of installation.

The name, address, telephone, facsimile, quotation or other reference of the manufacturer and of the specialist installer.

Operational instructions for the information of the user. Maintenance Instructions.

Note: The Contractor shall obtain the above information from the manufacturer of each item concerned.  The above information shall be provided within three weeks of receiving the contract for all electrical equipments.

Any sample submitted differs from required samples will be rejected without discount at the first time, after that any rejected item will be  with 2% discount each time.

# 2.0	Labels And Notices

2.1 General

All warning notices and signs that notify the public shall be in Arabic and English

2.2	Warning Notices

Each item of low voltage switchgear or each switchboard shall bear a warning notice 'Danger 380 Volts' in red letters not less that l3mm high in both Arabic and English.

  - Information Notices

Each item of switchgear and each distribution board shall bear a label indicating the circuit or circuits served by reference to an alpha numerical reference on the drawings, where applicable, and the name of the plant or area served

Such labels shall be of a minimum size 40mm X 15mm for MCBs and 120mmx30mm for MCCBs and shall be fixed by screws or rivets. Each label shall provide the following information

Item Number (if any)

Service – Lighting– Power etc.

Area Served

Phase

Labels for Electrical Boards shall be of a minimum size 250mm X 100mm and shall be fixed by screws or rivets. Each label shall provide Name of electrical board.

Labels shall be fixed to all Electrical equipment by the Contractor, whether or not the equipment was supplied by him.

2.4	Distribution Board Labels

Each distribution board shall have a fixed permanent label in the inside cover indicating the phase, rating and function of each outgoing way.

The labels shall be typed on heavy cartridge paper inserted in a transparent plastic envelope screwed to the distribution board. Labeling shall follow the As built drawing. The labels shall have a space for each spare way and the material of the label shall allow future users to mark in ink the function of spare ways as they are used.

Three type written copies of each label showing its origin shall be handed to the Engineer on completion.

During the progress of the Works temporary labels shall be used to record circuits as they are connected to each board.

2.5	Warning Labels

Where switches and / or accessories are adjacent to each other, but on different phase , a warning label 'volts adjacent' shall be fitted to the grid of and witch, and where accessories are concerned , if this is not possible, a Demo label shall be provided with the end wrapped round the live cable(s)

2.6	Earthing System Warning Labels

Every earthing lead must be protected against mechanical damage and have at its point of connection to the electrode or other means of earthing , a permanent label indelible marked with the works 'Safety Electrical Earth - Do Not Remove'

3.0	Testing And Inspection

3.1	Distribution System

Before completion, the installation shall be tested in accordance and to demonstrate compliance with the British IEE Regulations for Electrical installations and in accordance with the requirements of the Engineer.

Inspections will be carried out during installation and after completion of work.

All assistance in the form of Labor and instruments for carrying out such tests and inspections shall be supplied by the Contractor at reasonable times as required by the Engineer and the costs of such tests shall be included in the prices quoted by the Contractor for the various items to be installed under the specification.

The contractor shall allow for all final tests to be made in the presence of the Engineer who shall have been duly notified of the contractor’s intentions. The Engineer will require triplicate copies of test certificates covering all tests carried out on completed installations

All cables and cable sheaths shall be tested for continuity and insulation resistance as the work precedes and before connecting to the main supply.

The Testing procedures are as follows:

a. Ring Circuit continuity

b. Protective conductor continuity

c. Measurement of Insulation Resistance

d. Check of Protection by barriers and Enclosures.

e. Measurement of the insulation of Non conducting floors and walls.

f. Verification of Polarity

g. Measurement of earth Fault Loop Impedance

h. Test of Operation of Residual Current Devices

i. Tripping times of residual Current devices

All the above shall be carried out in accordance with the IEE Regulations for Electrical Installations. The contractor must show for each procedure and calculation and three copies issued to the Engineer after completion of each test.

After completing each part of the installation and after carrying out the above tests the contractor shall switch on all electrical loads.  The current in each phase shall be measured with a clip-on ammeter and if an imbalance of more than 10% exists reconnections shall be made to balance the load. Before final test are carried out on the whole or part of the installation, the contractor shall switch on all of the installation which is completed at that time. He shall switch on all loads and run the installation for a minimum period of three hours, at 1/3 full load and minimum period of a half hour at full load. Test certifications shall be of the form specified in the Regulations

Phase sequences shall be tested at each distribution board the tests shall show that the phase sequence and color coding is constant throughout the installation, the sequence being RY B.

Tests shall be made during and after installation to demonstrate that the phase rotation is correct at all end connections of power cables Where electronic equipment is installed, care must be taken when testing to avoid damage due to testing voltages . If necessary, vulnerable Plant and equipment must be disconnected.

3.2	Signal Cable

All signal cable shall be tested electrical contact exists between cores.

The insulation resistance between each conductor in the cable and all - other conductors and the screen or metallic sheath, there present, connected to each shall be tested and recorded before connection to apparatus or other cables.

When cable are supplied and laid under the same contract the electrical resistances of the cores shall be measured and the figures obtained shall not exceed the calculated resistance by more than 5%.

After the installation has been completed a check using 100 volt test set, that no ‘earth’s' or contacts between cores have been established during the connecting up.

4. Power Cables

4.1 PVC and XLPE Insulated Power Cables

The cables shall conform the BS6346:1969 IEC501-1 PVC Insulated Cables for Electricity Supply, which specifies requirements for cables operation at voltages up to and including 3.3 kV.

The cables shall conform generally to international requirements as defined in IEC standard 501-1 and suitable designs can be supplied to cater for the National Standards of other countries.  It is however not acceptable to use other national standards at random throughout the project.  The number and kind of international standards to be approved by the engineer.

All Cables should be Synergy American made.

4.2 XLPE Insulated Power Cables

The cables shall conform to LEC502-1983 and insulated power cables rated voltage from 1 KV up to 33 kV.  XLPE shall be of thermosetting compound, has superior resistance to deformation and to be operated at maximum temperature of 90 co.

Core Identification

Number or cores       Core colors

Three		              Brown, Brown with Orange line, Brown with yellow line

Four		              Brown, Brown with Orange line, Brown with yellow line, 
                                 (Green and Yallow)

4.3 Finish

The standard finish for all cables shall consist of an extruded black PVC oversheath which conforms to BS6346:1969 for thickness and to BS6746:1969 for properties.  The external surface is embossed with the voltage designation.

4.4 Standard Copper

These shall be high conductivity conductors which meet the requirements of the BS6360:1969 “Copper Conductors in Insulated Cables and Cords (metric nit)” Where possible, shaped conductors shall be compacted to reduce dimensions and give a smooth profile.

4.5 Fillers

PVC fillers are included between laid-up where necessary.

4.6 Bedding

For multicore cables with shaped conductors, the bedding may consist of either and extruded layer of PVC compound complying BS6476:1969 or two or more layer of PVC tape.  In cables having circular conductors the bedding is normally an extruded layer of PVC.

4.7 Conductors-XLPE

XLPE shall be of a thermosetting compound and compared with PVC, has superior resistance to deformation at high temperature enabling the cable conductor to be operate at a maximum continuous temperature of 90oc

4.8 Cable Specification

The cables shall be in accordance with I E C publication 502 1983 ‘Extruded solid dielectric insulated power cables for rated voltages from 1 kV up to 30KV’

4.9 Conductors

All cables shall be supplied with circular stranded conductors in copper or aluminum.  These conductors shall be compacted to reduce their dimensions and comply with IEC publication 228 ‘conductors of insulated cables’.

4.10	 Installation of PVC insulated Power Cables

The cables shall be of 600/1000 volt grade complying with BS6346:1969. Each cable shall be supplied in one length no through joint will be allowed without the written permission of the Engineer. The contractor shall be responsible for the correct measurement of all cable lengths.

Cables shall be delivered to site on drums. The size of cables and

Number of cores shall be as indicated in the calculations

4.11 	Installation of Cables

The contractor will perform the following instructions.

Installation of the cable in one length from main distribution to the different distribution panels:

- Arrangement of the cables and methods of installation shall be approved the engineer.

Vertical Ducts

Cables shall be supported by approved cleats or saddles .

Ceiling, Floor Space, and exposed service areas

Cable shall be supported by cable hangers securely fixed to the roof and walls on their supports.  In a neat and tidy manner coordinated with others services.  All arrangements to be commented on by the engineer.

4.12	  Testing

Immediately after installation, cables shall be tested with a 500 volt test set to demonstrate that the insulation resistance between cores and earth satisfactory.

4.13	  Clearance

150mm clearance shall be maintained between cables and any equipment, pipe work (including lagging) associated with other services.

Where this condition is unavoidable or difficult to comply with, the clients representative shall be informed prior to the installation being commenced otherwise the tenders may be requested to divert or adjust the fixing of any such cable affected.

4.14	   Bends

The bending radius of cables during installation shall be kept as large as possible, and no cables shall be allowed to be bent to a radius less than that specified in the relevant British Standards.

5.0	Cables

5.1	PVC Insulated Cables - Non Sheathed - Single Core

The cable shall be either solid or standard with plain copper conductors, PVC insulated.

Heat resisting PVC shall be provided where required voltage range 300/500v shall be to BS6004/1975 Table 3

5.2	PVC Insulated and Sheathed - Single and Multicore

the cable shall be either solid or standard with plain copper conductors   PVC insulated and PVC sheathed overall . An uninstalled plain copper earth continuity conductor shall be between the cable cores

5.3	Joint in Conductors

Joints conductors shall be made using insulated terminal blocks as specified in the section dealing with apparatus. The terminal blocks shall be contained in metal enclosures complying with this specification.

5.4	  General

The cables shall be looped progressively from point to point and no The joint and will be permitted. Cables emanating from different fuse boards switchfuses shall not be drawn into the same conduits or draw boxes.

The contractor shall ensure that multi compartment trunking has the dividers spaced to suit the numbers of cables.

All conductors shall be copper and one smaller than 1.5mm2 shall not be used. All sub-main cable and 3 phase sub-circuits shall have self-colored insulation in accordance with the given . Single phase lighting and power sub-circuits connected to 3 phase distribution board shall have self-colored insulation on the phase conductor to identify the phase to which it has been connected.

PVC cable color coding:

Brown	                           	240v red phase

Brown with Orange line	240v yellow phase

Brown with yellow line     	240 blue phase

Black	                                    Neutral

Greenwith yellow               	Earth

5.5	Cable Installation

Earth continuity conductors shall terminate in the earth terminal of the accessory or equipment. All earth wires shall be adequately sheathed with yellow/green PVC sheathing.

All cables shall be installed between items of equipment without joints looping of conductions shall be adopted throughout the installation Junction boxes will not be permitted without the prior approval of the engineer or his representative.

A bend on the cable shall, have a radius not less than four times the width of the cable.

Specification for UPS 3000VA Online

Qty: 1

| 3000 VA | Output power capacity |
| --- | --- |
| 2100 Watts | Output power capacity |
| Single phase with ground | Phase |
| sine wave | Waveform type |
| 220 Vac +/-2% | Nominal output voltage |
| 220 V | Nominal input voltage |
| 46/54 Hz | Input frequency |
| 50Hz +/-0.2% | Output frequency |
| 160 - 300 V at foul load | Input voltage range for main operations |
| 3:1 | Crest Ratio |
| 17.5minutes (1050 Watts) | Typical backup time at half load |
| 5 minutes (2100 Watts) | Typical backup time at full load |
| 0 - 40 °C | Operating Environment |
| - Automatic on over loud and failure - Voltage rang 80-264Vac | Bypass |
| - Ac to Dc : 0ms - Inverter to Bypass :2.5ms | Transfer time |
| sealed Lead-Acid battery with suspended electrolyte | Batteries |
| Load level – Battery level – Battery mode – Line mode – Inverter – Bypass – Overloud - Fault | Indicator Status |
| Over voltage limit protection ( turn off the input switch ) | Input voltage protection |
| Basic UPS signaling RS-232 cable, CD with software, User Manual | Accessories |
| IEC-320-C20 | Input Connection Type |
| (6)IEC 320 | Output Connections |

FORM OF

CONTRACT FOR WORK

(Construction)

between

TheInternational Committee of The Red Cross

hereinafter referred to as "the Client", represented by Mr. Patrick Gueissaz

and

xxxxxxxxxxxxxxxxxx

hereinafter referred as "the Contractor" represented by Mr. xxxxxxxxxxx

and

Ministry of Health,

hereinafter referred as "the Owner" represented by xxxxxxxxxxxx

# PREAMBLE

This projects aims at rehabilitation of the emergency department in shouhada Al Aqsa hospital . The works includes rehabilitation of construction elements, improving the lighting system, improve medical gases system, construction of x-ray room, and modifying follow of patients.

Ministry of Health (MoH) is the owner of the project.

# REPRESENTATION

Representative of the Client

Mr. Patrick Gueissaz, Head of ICRC Gaza Sub Delegation

Representative of the Contractor:

xxxxxxxxxxxxxxxxxxxx

Representative of the Owner:

xxxxxxxxxxxxxxxxxxxxxx

# OBJECT

## 3.1	Object of the contract

The object of this contract is to permit of necessary works aimed at modifying the current ED in Al Aqsa Hospital to meet the needs of new system, the work includes the following:

- Modify the flow of patients

- Modifying the lighting system

- Rehabilitation of needed infrastructure

- Installing new medical gases system

- Consruction of X- ray room

## 3.2	Contractual documents

The following documents constitute an integral part of the contract and must be signed:

    - Special conditions of the Contract (Enclosure 1)

    - ICRC General Conditions for work contracts (Enclosure 2)

    - Bill of quantities (BOQ) (Enclosure 3)

    - Technical Specification (Enclosure 4)

    - Drawings and Plans (enclosure_5)

    - Budget according to the Bill of Quantities (enclosure_6)

    - Time schedule with schedule of payments ( Enclosure 7)

## 3.3	Certification by the Contractor

Refer to General Conditions (Enclosure _2)

# START AND END OF WORKS

4.1	Duration of contract is 4 calendar months.

4.2	The Contractor will start the work on: ……….

4.3	The work is to be completed by: ……..

4.4	Conditions

4.4.1	For contract to come into force

The present contract comes into force from the date of signing by the contracting parties.

4.4.2	For the contract to come automatically to an end

The present contract becomes null and void in the following cases:

- if the works do not start within 7 days following the hand-over of the site to the Contractor

- if the Contractor stops the work for 10 days, without officially informing the Client and the site supervisor

- if the Contractor fails to correct a defect accordign to the supervisor instructions and within the set deadline of 7 days after reception of the notice.

Furthermore, refer to General Conditions (Enclosure_2- Article 18).

# PRICE

## 5.1	Price according to the BoQ

The total value of the works to be performed under this contract is xxxxxx, [xxxxxxxxxxxxxxxxxxxx Only], VAT exclusive. This value may change if the works effectively executed increase or decrease in comparison to the Bill of Quantities. However, unit prices indicated in the BoQ are fixed.

The Contractor guarantees that the variation will not exceed 5 % (five) of the total value of the contract.

## 5.2      Included in the prices

Refer to Bill of Quantities (Enclosure_3 - Article 3.2.3).

## 5.3      Taxes, duties

The ICRC is a tax exempted institution and therefore does not pay VAT.

The amount of the contract is exclusive of VAT. It is the Contractor's duty to provide a valid Zero VAT invoice, duly stamped by Ministry of Finance. Any taxes of whatever nature, including but not limited to VAT, shall be the sole responsibility of the Contractor.

Important note: Failure to produce valid zero invoice (with ministry of finance stamp) will result in a payment with a reduction of 10 % from the VAT excluded price. The deducted amount will be paid upon presentation of the zero VAT invoice.

## Payment

## Refer to Time schedule with schedule of payments ( Enclosure 7 – Article 3.2.7)

# OBLIGATION OF THE CONTRACTOR

Refer to General Conditions (Enclosure_2)

# OBLIGATIONS OF THE CLIENT

The Client ensures a close supervision of the work done by the Contractor.

The Client reservesits right to reject any material, equipment or work performed not meeting the standards required.

The Client must inform the Contractor of any changes in the scope of project and technical drawings within a suitable period of time, before the execution of the concerned works.

The client releases payments for the work performed by the Contractor in accordance with the order specified in article 5.4. of the present contract.

## 7.1	Contribution in terms of technical input (plans, etc)

Refer to Drawings and Plans (Enclosure_5 - Article 3.2.5)

## 7.2	Contribution in terms of equipment input

Not applicable.

## 7.3	Contribution in terms of work

Not applicable.

# SPECIAL CONDITIONS, RESERVED DECISIONS AND NECESSARY APPROVALS

MoH is the final beneficiary and owner of the project.

The Owner exerts rights of supervision over the implementation of the works and in particular:

- The Owner will approve testing of materials and equipment used by the Contractor.

- The Owner will assign a qualified Engineer as supervisor at the construction site. The Engineer will report on implementation of daily tasks by the Contractor to the Owner and coordinate with the Client.

- The Owner and the Client Engineers will inspect each part of the construction work. Each part of the project must be inspected before starting a new part. This concerns especially the hidden constructions and systems that must be tested before covering them.

- The Owner will check and approve measurement sheets according to the progress of work

- All payments will be released upon certification of satisfactory performance by the Owner and the Client Engineers.

At the end of the project, the Owner will form a committee to which the project will be handed over once completed.

In case of Force Majeure or any other event that are beyond the reasonable control of Contractor, which makes the performance of its obligations hereupon impossible  the Contractor should submit beforehand to the Owner and the Client a written notice explaining the reasons and the delays. If accepted by the Owner and the Client, this notice will amend the present contract.

# MODIFICATIONS: ADDITIONAL AND / OR ELIMINATED WORKS

Refer to General Conditions (Enclosure_2 - Article 7)

# FINANCIAL GUARANTEES

## Performance bond

The Contractor undertakes to deliver to the Client, before the start of the works, a performance bond in the form of a first demand guarantee, issued by a first class banking establishment and valid up to the date of the provisional acceptance of the project.

The amount of the performance bond will correspond to 10 % of the price of the works exclusive of taxes, namely NISxxxxxx, [xxxxxxxxxxxxxx NIS Only]. The cost of issuing the guarantee will be borne by the Contractor.

## Advanced guarantee

20% of the contract amount to be released as advance payment on the works, not later than 30 days after the signature of the contract by all parties and giving that the Contractor has signed an unconditional Bank Guarantee (AdvancedGuarantee) at the name of the Client equivalent to the same amount of the advance payment.

## Retentions during the works

## Refer to Time schedule with schedule of payments ( Enclosure 7 – Article 3.2.7)

## Return of retentions and performance bond

The retention will be paid and the performance guarantee will be returned entirely at the satisfactory completion of the project as soon as:

- The certification of provisional acceptancetakes place by the Client and the Owner.

- The final statement of account and measurement sheet has been accepted.

- And the maintenace guarantee referred to in Article 10.5 has been supplied.

## Maintenance guarantee

After provisional acceptance, the Contractor shall provide the Client with a maintenance bank guarantee for an amount equivalent to 10% of the total amount of the whole works executed by way of guarantee against any faults, which may appear before final acceptance.

This 10% will be kept for one year after the completion of the project, and can be in cash or as a bank guarantee at the name of the Client providing it is issued by one of the following banks:

- The Arab Bank

- The Amman Cairo Bank

- The Bank of Palestine

The guarantee must remain valid up to the final acceptance of the project, one year after the provisional acceptance.

# SUBCONTRACTING

Refer to General Conditions (Enclosure_2 - Article 8)

# INSURANCE AND LIABILITY

Refer to General Conditions (Enclosure_2 - Article 14)

## Construction works insurance

The Contractor guarantees that it has concluded construction works insurance contract and that it will pay the related premiums.

The Client will receive certification from the insurer concerning the all-in price and the delegation of payment.

## Third party liability

Insurance, including for third party liability, and for all other liabilities which may result in consequence of the works, shall be the sole responsibility of the Contractor. The Contractor accepts full responsibility to be insured against any such liabilities which may occur. The Client accepts no responsibility for any liabilities which may result in consequence of the works.

Furthermore, refer to General Conditions (Enclosure_2 - Article 14)

# PENALTIES

Failure by the Contractor to fulfill the contract by the agreed dates will result in the Contractor being penalized as follow:

- one week or part there of late: 0.5 % reduction of the total value of the contract

- two weeks or part there of late: 1 % reduction of the total value of the contract

- three weeks or part there of late: 2.5 % of the total value of the contract and for every week or part there of thereafter a future reduction of 2.5 % per week to a maximum of 10 %.

Furthermore, refer to General Conditions(Enclosure_2- Article 13)

# LANGUAGE

If this contract is translated into another language, the english version will prevail in case of dispute or discrepancy.

# APPLICABLE LAW

Swiss law governs this contract, the clause of arbitration if any, and the arbitration procedure exclusively without regard to conflicts principles.

# ARBITRATION

This contract is subject to arbitration exclusively, according to the attached General Conditions.

# MODIFICATIONS OF THE CONTRACT / GENERAL CONDITIONS

Article 4.1 [Duration of Contract] is added to the present contract.

Article 5.4 [Payment] of this contract is modified as follows:

The price of the works is payable, during the implementation period, according to the real progress of works and the measurement sheets approved by the Client and the Owner.

All payments will be made by bank transfer by the Client Office to the Contractor. To this effect, the Contractor shall provide the Client with a bank statement at his name mentioning clearly the bank address, and the account owner's name and number.

Payment shall be made in NIS, no later than 30 days following contractor submitted payment being approved by the Client and the Owner.

Summary of payments:

- 20 % of the contract amount to be released as advance payment on the works, not later than 20 days after the signature of the contract by all parties and giving that the Contractor has signed an unconditional Bank Guarantee (advance guarantee) at the name of the ICRC equivalent to the same amount of the advance payment.

Following payments will be released monthly during the implementation period, according to the progress of the works and the measurement sheets approved by the Client and MoH. 20% of these payments will be kept back by the Client, corresponding to 20% for the repayment of the advanced payment.

Furthermore, refer to General Conditions (Enclosure_2 - Article 17).

Article 10.2 [Advanced Guarantee] is added to the present contract.

Article 10.3 [Retentions during the works] is modified as follows:

The Client will retain 30 % from payments, except advanced payment, corresponding to 20% for the repayment of the advanced payment and 10% as a retention fee, which amount is kept by the Client until the completion of the works.

Enclosures to be signed:

-	Documents mentioned in article 3.2 "Contractual documents"

For information

-	Rules to be observed by individuals who work for the ICRC

Signed at 	______________________	on	________________________

For the Contractor:	For the Client

______________________	________________________

xxxxxxxx	Mr. Patrick Gueissaz

Manager					        Head of Sub-Delegation

________________________

Mr. Laurent- Thomas Poli

Head of Project

For the Owner

________________________

xxxxxxxxxxx

The term "Contractor" stands for both men and women.