Palestinian National Authority

##### Ministry of Health

###### Procurement Department

Rehabilitation of European Gaza Hospital Wastewater Treatment Plant

Financed by: International Committee of the Red Cross ICRC

Tender No.: 51 /2013

TABLE OF CONTENT

Press Advertisement	3

Invitation for Tender	4

Special Conditions of Contract	5

General Conditions	8

Schedule of Requirements (BoQ)	23

Technical Specifications	26

Press Advertisement

Palestinian National Authority

Ministry of Health

General Directorate for Admin. &Finance

Procurement Department

Invitation for Tender no. (51 /2013)

“Rehabilitation of European Gaza Hospital Wastewater Treatment Plant” project

Funded by International Committee of the Red Cross

- Ministry of Health invites sealed tender from eligible suppliers for implementing the project of Rehabilitation of European Gaza Hospital Wastewater Treatment Plant Funded by the International Committee of the Red Cross (ICRC).

- Interested eligible suppliers may obtain further information and inspect the tender documents at address below; from 8:00 am to 14:00 pm.

- A complete set of tender documents in English may be purchased by interested contractors on submission of a written application and upon payment of a non-refundable tender fee of only (300) NIS. The method of payment will be a check against receipt of voucher.

- Interested contractors should be registered at Contractors Union; classification should not be less than second class in water and wastewater infrastructure.

- Tender must be delivered to the address below by 11:00 a.m. on May 5, 2013.

- Pre-bid meeting will be held in EGH hospital at    10:00 am on April 30, 2013

- All prices are in Shekel and VAT excluded. The awarded contractor should provide Zero VAT invoice duly stamped by MoF

- All tenders should be accompanied by a Bid Security equal to 5% of the total tender value from a local Bank, and should be issued in English and by the name of International Committee of the Red Cross (ICRC).

- Tender will be open immediately thereafter, in the presence of the suppliers who choose to attend at the same address at which a supplier chooses to submit his tender at Sunday on 11:00 a.m. May 5, 2013

- Awarding contract will follow ICRC/MoH rules and not necessary the lowest price

- The successful contractor will pay advertisement fees.

- For more information, suppliers could contact:

Procurement Department, 1st floor at the Administrative Companion

Ministry of Health, Administrative Companion

El Wehda Street, Remal,

Gaza,

Tele:08 -2824607,08-2838553,Fax: 08-2827634

- E-mail:  purch@moh.gov.ps

- contact:

- Procurement Department, 1st floor at the Administrative Companion

- Ministry of Health, Administrative Companion

- El Wehda Street, Remal,

- Gaza,

- Tele:08 -2824607,08-2838553,Fax: 08-2827634

- E-mail:  purch@moh.gov.ps

Invitation for Tender no. (51/2013)

Palestinian National Authority

Ministry of Health

General Directorate for Admin. &Finance

Procurement Department

Project of Rehabilitation of European Gaza Hospital Wastewater Treatment Plant

Funded by International Committee of the Red Cross

- Ministry of Health invites sealed tender from eligible suppliers for implementing the project of Rehabilitation of European Gaza Hospital Wastewater Treatment Plant Funded by the International Committee of the Red Cross (ICRC).

- Interested eligible suppliers may obtain further information and inspect the tender documents at address below; from 8:00 am to 14:00 pm.

- A complete set of tender documents in English may be purchased by interested contractors on submission of a written application and upon payment of a non-refundable tender fee of only (300) NIS. The method of payment will be a check against receipt of voucher.

- Interested contractors should be registered at Contractors Union; classification should not be less than second class in water and wastewater infrastructure.

- Tender must be delivered to the address below by 11:00 a.m. on May 5, 2013.

- Pre-bid meeting will be held in EGH hospital at    10:00 am on 30/04/2013

- All prices are in Shekel and VAT excluded. The awarded contractor should provide Zero VAT invoice duly stamped by MoF

- All tenders should be accompanied by a Bid Security equal to 5% of the total tender value from a local Bank, and should be issued in English and by the name of International Committee of the Red Cross (ICRC).

- Tender will be open immediately thereafter, in the presence of the suppliers who choose to attend at the same address at which a supplier chooses to submit his tender at Sunday on 11:00 a.m. May 5, 2013

- Awarding contract will follow ICRC/ MoH rules and not necessary the lowest price

- The successful contractor will pay advertisement fees.

- For more information, suppliers could contact:

Procurement Department, 1st floor at the Administrative Companion

Ministry of Health, Administrative Companion

El Wehda Street, Remal,

Gaza,

Tele:08 -2824607,08-2838553,Fax: 08-2827634

- E-mail:  purch@moh.gov.ps

Section I.

Special Conditions of Contract

| 1. Tender Currency | The unit rates and prices shall be quote by the Contractor entirely in NIS. |
| --- | --- |
| 2. Tender Prices | The Contract shall be for the whole Works, as described in the schedule of requirement and technical specifications. |
| 3. Bid Validity | Tenders shall remain valid for the 90 days starting from the date of tender opening. |
| 4. Bid Security | All tenders should accompanied by a Bid Security equal to 5% of the total tender value, and should be issued in English and by the name of Ministry of Health (MoH) from a local bank. |
| 5. Performance Security | The successful Contractor should deliver to the Client a Performance Security for 10% of total value of the contract in the form of Bank Guarantee issued at the successful contractor's option by a local bank; and should be issued by the name of the International Committee of the Red Cross (ICRC) |
| 6. Maintenance Guarantee | Contractor should deliver Maintenance Guarantee by the end of the project 10% of the total amount of the contract, the guarantee should be issued from the approved banks ( please refer to ICRC contract) in the name of ICRC |
| 7. Signing contract | Within 7 days after receipt of the Letter of Acceptance, the successful Contractor shall sign the contract |
| 8. Time Control | The Contractor shall start his program for the Works within 7 days from the date of signing the contract and hand over the contract. |
| 9. Withdrawal from offers | If the winner contractor withdraws, he will loose the bid security guarantee attached with the offer. |

Special Conditions of Contract

| 9. Contents of the Proposal Documents | 1.Advertisment 2.Invitation to Tender 3.Section I. Special Conditions of Contract 4.Section IIGENERAL CONDITIONS 5.Section III Schedule of Requirements (BoQ) 6.Section IV Technical Specifications 7.Form of Contract |
| --- | --- |

Special Conditions of Contract

# Section II

GENERAL CONDITIONS

INTERNATIONAL COMMITTEE OF THE RED CROSS

GENERAL CONDITIONS

CONTRACTS FOR WORK

1. DEFINITION.		11

2. OBLIGATION OF THE CONTRACTOR.		11

2.1. General		11

2.2. Certification		11

2.3. Compliance with professional standards		11

3. MATERIALS		12

4. SAMPLES		12

5. CONCEALED WORKS		12

6. INFORMATION		13

6.1. Right of inspection		13

6.2. Site meeting reports		13

6.3. Final report		13

7. MODIFICATIONS: ADDITIONAL AND / OR ELIMINATED WORKS		13

7.1. Principles		13

7.2. Price		13

8. SUBCONTRACTING		14

8.1. Principle		14

8.2. Payment of Subcontractors		14

8.3. Obligations of the Subcontractors		15

9. ASSIGNMENT		15

10. ACCEPTANCE PROCEDURE / GUARANTEE FOR DEFECTS		15

10.1. Notice of completion of work		15

10.2. Defects		15

10.3. Repairs		16

10.4. Provisional acceptance		16

11. FINAL ACCEPTANCE / WARRENTY		16

12. FIXED PRICE CONTRACTS		16

13. PENALITES		16

14. INSURANCE		17

15. PLEDGE OF DISCRETION / ICRC NAME AND LOGO		17

16. INTELLECTUAL PROPERTY RIGHTS		17

17. PAYMENT		17

18. CANCELLATION OF THE CONTRACT		18

18.1. In general		18

18.2. For exceeding of estimates		18

18.3. Consequences of the cancellation		18

19. CANCELLATION AGAINST INDEMNIFICATION		18

20. FORCE MAJEURE		19

21. RESPECT FOR HUMANITARIAN VALUES		19

22. WORKING CONDITIONS AND CHILD LABOUR		19

23. RESPECT FOR THE LAW		19

24. MINES AND OTHER WEAPONS		20

25. SECURITY WARNING / DISCHARGE FROM LIABILITY		20

26. MODIFICATIONS OF GENERAL CONDITIONS AND / OR CONTRACT		20

27. ENFORCEABILITY / VALIDITY		20

28. ARBITRATION		20

29. IMMUNITY		21

# DEFINITION

A contract for work is an agreement whereby the Contractor obligates himself to produce a work, and the Client to pay the price.

# OBLIGATION OF THE CONTRACTOR

## General

The Contractor shall protect the interests of the Client and perform the work and have them performed in accordance with the documents referred to in the contract and shall draw up any other supplementary or detailed plans which may be necessary for the performance of the contract.

He is obligated to carry out the work personally or to have it carried out under his personal direction.

## Certification

The Contractor certifies that it has:

- Visited and inspected the site and location of the works

- Taken full and entire note of the plans and descriptions

- Verified the plans and the preliminary bills of quantities

- Asked for all and any necessary or relevant information, pertaining to and for the calculation of its all-included price.

## Compliance with professional standards

The Contractor must apply the same care and knowledge one may expect from a professional and diligent contractor in the same line of work taking all necessary precautions, respecting his contractual obligations and applying state of the art rules.

In the absence of an agreement to the contrary or custom, he shall himself provide for such accessories, instruments and equipment as shall be necessary for the carrying out of the work.

The Client has the right to reject any material, equipment or work performed not meeting the standards as stated in the contract.

In particular the Contractor shall:

2.3.1	Ensure a high quality level of work in accordance with the national standards for civil and mechanical work. The Contractor will have the work executed only by an experienced labour force.

2.3.2	Ensure a close supervision of the work quality with a qualified engineer as supervisor where necessary during the entire duration of the work.

2.3.3	Bear full responsibility for implementing all safety procedures in compliance with all applicable safety and labour laws, and bear full responsibility for any accidents arising from the normal execution of the work.

2.3.4	Ensure that local services are disrupted for the minimum duration of time during the work, and coordinate with the relevant authorities in order to warn any potentially affected people of any necessary shutdowns.

2.3.5	Clean the site and take good care of it during the work. All debris, garbage, waste materials and construction equipment, used during the project must be taken out of the work site on termination or completion of the contract.

2.3.6	Keep, of its own volition, the Client informed of unforeseen or significant occurrences or difficulties, particularly in the event of a delay in the work and supply the Client with the information the latter requests.

# MATERIALS

To the extent that the Contractor has undertaken to supply the material, he is liable to the Client for the quality and is bound by a warranty in the same manner as a seller.

If, during the carrying out of the work, defects become evident in the material supplied by the principal or with regard to the designated construction site, or other conditions develop which endanger a due and timely carrying out of the work, the Contractor shall without delay notify the Client thereof, otherwise he bears the adverse consequences himself.

# SAMPLES

The Contractor shall without additional charge whenever requested by the Client supply samples for selection or quality control purposes. Such supply and the selection by the Client shall be effected in good time to ensure that no delay results.

4.1	All workshop or laboratory tests will be at the Contractor's expenses. The Contractor will provide the results for acceptance by the Client within three days after the testing.

4.2	The Contractor must submit any pumping equipment for testing one week prior to its use on-site to an agreed workshop specified by the Client.

# CONCEALED WORKS

All parts of the work that will be hidden from view are to be inspected by the Client prior to their covering. At the Client's request, the Contractor must uncover any hidden work for further inspection or testing.

# INFORMATION

## Right of inspection

The Client shall have the right to inspect the progress and performance of the work, as well as its quality and that of the materials being used.

The Client's right of inspection shall not in any way relieve the Contractor of its responsibilities for the performance of the work.

## Site meeting reports

The Contractor shall hold regular site meetings, to which the Client shall be invited. In any event, the minutes of the meetings shall be sent to the Client.

## Final report

When the work is concluded, the Contractor shall deliver to the Client, free of charge, the file certified by the Contractor containing the operating instructions, together with all the necessary plans, duly updated and certified, where necessary, by the Contractor's architects and engineers. These shall include in particular:

- Paper of electronic drawings of the plans implemented

- Diagrams and operating instructions for all installations

- A list of the subcontractors and their contact details.

# MODIFICATIONS: ADDITIONAL AND / OR ELIMINATED WORKS

## Principles

If the Client wishes to change, amend or improve the work it must provide the Contractor with a written request in good time.

To determine the feasibility, the increase or reduction in prices and the impact on delivery dates, the Contractor will have a period of fifteen days from receipt of the request to draw up a detailed written offer showing whatever effect the modification might have on the work.

The desired modification will be carried out and paid for only if the Client has accepted the conditions, delivery dates and impacts on the initial work in writing.

If the Contractor refuses the modifications for feasibility or deadline reasons in spite of the Client assuming responsibility for all consequences in connection with the modifications, the Client may have the modifications executed by a third party.

## Price

The additional work necessitated by the modifications or improvements referred to above will be calculated on the basis of the unit prices taken into consideration for fixing the price of the work, including any discounts.

Work, which will be eliminated, will be deducted from the price, on the basis of the unit prices used when calculating and fixing the price of the work, excluding any discounts. Compensation has to be paid to the Contractor for any loss of earnings due to this elimination.

If the parties cannot agree on the cost of any additional work, the Client shall have the right to invite competing tenders and, if necessary, impose the resulting prices on the Contractor.

# SUBCONTRACTING

## Principle

The Contractor may sign contracts for work with tradesmen, contractors and suppliers (hereinafter referred to as "Subcontractors"), as well as with any other agents taking part in the work.

The Contractor will make such contracts in its own name and for its own account. Vis-à-vis the Subcontractors and agents, the Contractor shall have all the rights and prerogatives of a Client. Towards the Client, the Contractor remains entirely liable for any work executed by such third parties as if he had executed the work himself.

The Contractor does not have the right to hire any employee of a relevant ministerial authorities, ministerial sub-directorates, or of relevant municipal agencies, nor any member of any governmental agency or institution.

The Contractor must provide the Client with the business name of any Subcontractor or agent to whom it is intended to award a job so as to enable the Client, where applicable, to state its reservations. The Client may object to them only on reasonable grounds.

The fact that the Contractor awards a job to a subcontractor proposed but not imposed by the Client shall not relieve the Contractor of any of its obligations, responsibilities or liabilities.

## Payment of Subcontractors

The Contractor undertakes

8.2.1	to use the Client payments only for invoices in relation to the construction of the work

8.2.2	to pay the Subcontractors punctually for the amounts due to them

8.2.3	to produce a statement of its payments to the Subcontractor at any time upon simple request.

To permit compliance with this obligation to be checked, the Contractor may be requested to open a special account with a banking institution designated by the Client.

The Client shall have the right to make full and final payment directly to the Subcontractor of the amount agreed between the Contractor and the Subcontractor. The amount thus paid will be charged by the Client to the remuneration owed by him to the Contractor. In the event of a dispute over an amount between the Contractor and the Subcontractor, the Client shall be entitled to have the amount placed on deposit with the effect of full and final settlement vis-à-vis the Contractor.

## Obligations of the Subcontractors

The Contractor will ensure that the following provisions are included in all contracts concluded with its subcontractors:

8.3.1 	The Subcontractor undertakes to carry out the work personally using its own resources such that, as a rule, further subcontracting is excluded.

8.3.2	The Subcontractor guarantees the same high quality of work as the Contractor, respecting laws and professional standards one might expect from a professional in the same line of  work.

8.3.3 	Exceptionally, the Subcontractor may be permitted by the Contractor to sub-subcontract a part of the work, on condition that written authorisation has been sought and granted by the Client.

8.3.4 	If, by way of exception, the authorization to sub-subcontract is granted, the Subcontractor shall remain as liable for the work of its Sub-Subcontractor as it is for its own.

# ASSIGNMENT

The Contractor may not assign all or any part of its rights and obligations under this contract to a third party, save with the written consent of the Client given expressly and in advance.

# ACCEPTANCE PROCEDURE / GUARANTEE FOR DEFECTS

## Notice of completion of work

The Contractor will inform the Client that the work has been completed and call a meeting for the examination and provisional acceptance of the work. The parties will draw up a report noting the result of the examination.

In any case, the Client shall, as soon as appropriate according to usual business practice, examine the quality of the work and immediately notify the Contractor of defects, if any.

## Defects

If defects are noted, the Client will set a time limit for the Contractor to remedy them. A defect is the absence of a quality promised by the Contractor or which the Client was entitled to expect under the rules of good faith.

If the defects are not remedied within the said time limit, the Client may:

- either make a corresponding reduction of the price

- or have the defects remedied by a third party at the Contractor's costs and deduct the costs from the letter of guarantee.

Where the work suffers from defects which are so substantial, or deviates from the contractual specifications to such an extent, that it is unusable for the Client or that its acceptance cannot reasonably be expected of him, the Client is entitled to refuse acceptance and to cancel the contract (art. 18.3 "Consequences of cancellation" applies).

## Repairs

The defects repaired must be accepted in accordance with the above procedure.

## Provisional acceptance

- If the completion of work report does not note any defects, or

- If the Client has accepted the work in the completion of work report or by omitting to examine and notify defects in due time, or

- If a report confirms that the repairs have been properly carried out,

the work will be provisionally accepted.

# FINAL ACCEPTANCE / WARRENTY

Final acceptance of the work will be pronounced one year after the provisional acceptence (Warranty Period), provided that no defect is discovered. The discovery of minor faults will not prevent final acceptance but will give rise to a new notice of completion for the part of the work concerned. The discovery of major faults will prevent final acceptance and will give rise to a new notice of completion.

The warranty does not cover damages due to misuse, user's negligence, wear and tear or any other damages due to risks to be borne by the Client according to normal business practices.

Irrespective of final acceptance, the Contractor shall remain liable for a period of five years for defects which during the reception and proper examination were not perceptible or were intentionally concealed by the Contractor.

# FIXED PRICE CONTRACTS

If the compensation has been precisely stipulated in advance (fixed price), the Contractor is obligated to complete the work for this sum and may not claim an increase even if he had more labour or larger expenditures than had been foreseen.

If, however, extraordinary circumstances which could not have been foreseen or which were excluded from the assumptions made by both parties, impede the completion or render it exceedingly difficult, the judge may, in his discretion, authorize an increase of the price or dissolution of the contract.

The principal shall also pay the full price if the completion of the work has caused less labour than had been foreseen.

# PENALITES

The penalty clause, if any, will be imposed for late completion of the contract unless due to Force Majeure without prejudice to other measures stipulated in the contract such as early termination. Nevertheless, the Contactor must inform the Client immediately in the case of possible delays or Force Majeure in order to enable the Client to take any appropriate measures.

The Client has the right to deduct the penalty without further process either from any outstanding bills or from the retention to be returned or use it to compensate any claims the Contractor might have against him.

Even if the penalty clause is applied, the Client may still choose to cancel the contract according to these General Conditions.

# INSURANCE

Nothing in the parties' relations shall be construed as an employment relationship. The Contractor therefore bears sole responsibility for insurance (old-age, invalidity, unemployment, accident, sickness, loss of earnings, third-party liability), for which he shall take out adequate coverage for himself and his employees.

# PLEDGE OF DISCRETION / ICRC NAME AND LOGO

The objective of the ICRC is to provide protection and assistance for victims of war, civil war or internal disturbances and for other victims on whose behalf the ICRC is called upon to take action. To attain this objective as effectively as possible, the ICRC must at all times enjoy the confidence of governments and of the victims.

This confidence is largely based on the neutrality of the ICRC and on the discretion with which it conducts its activities and, in particular, on its undertaking that any body active for the ICRC will never disclose what he sees or learns while working for the ICRC.

Accordingly, anybody active for the ICRC therefore undertakes to observe the utmost discretion concerning matters with which he shall be called upon to deal or which may come to his knowledge and to consider himself bound by professional secrecy in this regard.

This duty shall remain in effect even after the contract has ended.

The use of the name and / or logo of the ICRC in any way is prohibited unless expressly authorised in writing in advance.

# INTELLECTUAL PROPERTY RIGHTS

The Contractor herewith automatically cedes to the ICRC all transferable intellectual property rights to the results of his work for the ICRC. These rights include, but are not limited to, the exclusive right to use, publish, sell, modify or distribute any material prepared for or on behalf of the ICRC.

# PAYMENT

The conformity of the scheduled payments to the real progress must be certified by the Contractor. This certification must be attached to each invoice so that the Client can verify the situation.

The time limit for payment is 30 days from the date of receipt of the invoice from the Contractor.

The Client may require that the payment be made into a specicial construction account with a specific bank, so as to ensure that the money is properly used and, particularly that payment is received by the various subcontractors.

By way of guarantee, the Client may retain an agreed percentage of the value of each invoice.

In the event of unjustified delay by the Client in paying an invoice, the Client will be liable to pay the Contractor the National Bank default interest rate with effect from the date of formal notice by the Contractor, as well as any bank loan charges to the Contractor.

No adjustment to the price of the Contract will be made due to variations of the exchange rates.

# CANCELLATION OF THE CONTRACT

## In general

If, during the carrying out of the work, the performance of either party can definitely be anticipated to be faulty or otherwise in breach of the contract, then the innocent party may set an appropriate time limit for a remedy, with the warning that, in the event of the other party's failure to perform the correction or continuation of the work, the contract may be cancelled. The Client has also the choice to give the work to a third party at the Contractor's risk and cost.

Either party may cancel this contract if the other party becomes insolvent.

## For exceeding of estimates

If an approximate estimate of the price or the time frame for the completion of the work agreed upon with the Contractor is exceeded disproportionately without interference of the Client, the latter is entitled, during as well as after completion of the work, to cancel the contract.

## Consequences of the cancellation

In the event that the contract is terminated, the parties return to each other what they have already received. If the work or part of it can not be returned and if it is of value to the Client, the later shall pay an equitable compensation. The same applies where constructions on real property could only be removed at a disproportionate disadvantage for the Contractor.

Claims for damages and / or interests are reserved.

# CANCELLATION AGAINST INDEMNIFICATION

As long as the work is incomplete, the Client may withdraw at any time from the contract, against compensation for the work already performed and against full indemnification of the Contractor's loss of earnings.

# FORCE MAJEURE

Neither of the parties shall be held liable for a delay or any other failure to perform brought about by unforeseeable natural disaster, civilian unrest, strike or government restriction / constraint independent of the will of the party invoking it, provided that said party:

- informs the other party immediately of the existence of the cause and potential delay, and

- does all it can to discharge its obligations in spite of that cause.

If the cause persists for seven days, either of the parties may cancel the contract by informing the other party in writing (art. 18.3 "Consequences of cancellation" applies).

# RESPECT FOR HUMANITARIAN VALUES

For the duration of the contract, the undersigned may according to the circumstances be considered “close” to the ICRC. His acts and/or behaviour may reflect on the image and/or the reputation of the ICRC. He therefore undertakes to comply with the essence of the relevant ICRC rules of conduct and to adopt an attitude compatible with the purely humanitarian nature of the organization’s work, in accordance with the attached “Rules to be observed by individuals who work for the ICRC”. This does not mean, however, that the undersigned, who remains self-employed, thus establishes an employment relationship with the ICRC.  The latter may cancel the contract if the undersigned does not respect these rules and/or if ICRC's association with the undersigned is detrimental to ICRC's actions or reputation (art. 18.3 "Consequences of cancellation" applies).

# WORKING CONDITIONS AND CHILD LABOUR

22.1	By virtue of the Universal Declaration of Human Rights, the Convention on the Rights of the Child and the ILO's Declaration on Fundamental Principles and Rights at Work, the Contractor must respect the following:

- prohibition on the use of child labour;

- prohibition on the use of forced labour;

- national laws regarding hygiene, safety and labour rights.

22.2	The application of these principles shall be based on the laws of the country in which the work is located.

22.3	Should those laws fail to be observed by the Contractor and / or its Subcontractors or suppliers, the Client may make recommendations. If these are not followed, the Client shall be entitled to suspend or cancel the contract (art. 18.3 "Consequences of cancellation" applies).

# RESPECT FOR THE LAW

The Contractor undertakes to comply with the law. Should he nevertheless fail to do so, the Client shall be entitled – depending on the seriousness of the breaches and the significance which he judges those breaches to have had regarding the ICRC's operations – to cancel the contract (art. 18.3 "Consequences of cancellation" applies).

# MINES AND OTHER WEAPONS

The Contractor hereby certifies not to be involved in any manner whatsoever in the transport, sale and / or production of mines or any other weapons. Should the Contractor make a false certification in this respect, the Client shall be entitled to cancel the contract with immediate effect (art. 18.3 "Consequences of cancellation" applies).

# SECURITY WARNING / DISCHARGE FROM LIABILITY

The nature of the ICRC’s work and of armed conflicts can make working for the ICRC highly dangerous. Risks include injury, kidnapping and death. Contractors must be aware of these risks and know that in case of a kidnapping it is ICRC policy not to pay any ransom and that no insurance has been concluded for that purpose. The Contractor confirms that he has been informed of and accepts these risks. In any case, the ICRC’s and its employees' liability is expressly excluded.

The Contractor must be thoroughly familiar with any specific instructions that apply at the delegation and comply with them at all times.

# MODIFICATIONS OF GENERAL CONDITIONS AND / OR CONTRACT

No modification of the clauses of these General Conditions or of the Client's standard contract may be effected without the express written agreement of both parties.

# ENFORCEABILITY / VALIDITY

Any provision of the contract prohibited by or unlawful or unenforceable under any applicable law shall to the extent required by such law be ineffective without modifying the remaining provisions of the contract.

Where however the provisions of any such applicable law may be waived they are hereby waived by the parties hereto to the full extent permitted by such law to the end that the contract shall be a valid and binding agreement enforceable in accordance with its terms.

# ARBITRATION

If the contract provides for arbitration, any dispute, controversy or claim arising out of or in relation to the contract, including the validity, invalidity, breach or termination thereof, shall be finally and exclusively settled by arbitration in accordance with the UNCITRAL (United Nations Commission on International Trade Law) arbitration rules in force on the date when the Notice of arbitration is submitted in accordance with these Rules.

Appointing authority shall be the Chamber of Commerce and Industry of Geneva, Switzerland.

The arbitral proceedings shall be conducted in English.

# IMMUNITY

Nothing in these General Conditions and/or in the contract shall be directly or indirectly interpreted as a waiver on the part of the ICRC of its privileges and immunities as an international organization.

Read and accepted:

Place and date:______________________	Signature:	________________________

# Section III

Schedule of Requirements (BoQ)

Schedule of Requirements

| S/N | Description | Unit |  |  | Qty. | Unit price NIS | Total price NIS |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Contractor shall take into consideration that all direct and indirect works and expenses (including dumping fess if needed) required for the completion of the coming items is included in the unit prices. The location of the works is European Hospital Treatment Plant, All works shall be carried out according to specifications, conditions of contract, and as directed by supervision Engineer. Any damages result from the contractor's activities should be fixed and cleared on his expenses. The contractor has to clean and remove all the debris, blocks, sand and other surplus materials resulted from his work. All the works should be performed with a complete coordination with the operating staff to avoid any flooding and disturbances of the plant operation schemes, and carry out all safety measures required during his work. The contractor has to make grid survey before starting the work and after finishing the work and to be approved by the supervisor engineer. The first reference datum for measurements of grid survey should be measured after removing grasses and plants from the pond and the second after excavation and finishing the work. |  |  |  |  |  |  |
| 1 | Evacuate the ponds , clean, and transport the settled materials to Sofa solid waste dump site , or any approved site, the cost fees are included in the item. Contractor has to bypass all the ponds through transporting the flow to existing lagoons and/or by trucks to KhWWTP, all fees and consequences should be part of the unit cost. |  | LS | 1 |  |  |  |
| 2 | Repair HDPE Sheets works include: - Cut; fill with mortar, reallocate, & weld the HDPE sheets as per manufacture requirements. - Contractor should where ever it is required to supply the same HDPE sheeting to cover any shortage in the sheets. - Supply necessary adhesive material to fix the sheets to the concrete walls. - Supply stainless steel or Aluminium plates with thickness not less than 5 mm to fix the sheets to the concrete walls - All the above works should be included in the unit price and the final approved works must be according to Engineer’s instructions and upon his approval. Contractor should include any required work to finalize the work as per the Engineer approval. |  | M2 | 600 |  |  |  |
| 3 | Supply and lay cast reinforcement concrete B 250 with a reinforcing mesh Ø 8 @15 cm, as an apron 1.2 meter wide 10 cm thick works include: 3.1 Cutting the existing sheets roll it & locate it within the concrete with rebars. 3.2 Construct reinforced beam as a key at the centreline of the aprons (20/20) 3.3 Construction joints each 2 meter (10 cm depth,2 cm width)filled with mastic joint 3.4 Supply and lay cement sand mix to fill the holes below the HDPE lining at the apron. |  | LM | 150 |  |  |  |
| 4 | Cleaning the whole wastewater treatment plant site from debris, trees and solid waste and transport it to the solid waste dump site at Sofa or any approved site , the fees are included in the item. |  | LS | 1 |  |  |  |
| 5 | Repair the fence and the gates. Contractor should visit the site and estimate the amount need to be repaired. No accessibility to the site should remain except the gates. |  | LS | 1 |  |  |  |
| 6 | Painting works The items( Painting works) include the supplying of all required material (paints, putty,….,) approved from Authorized institutions and workmanship. The walls and other elements to be painted should be cleaned. The color is according to the Engineer approval. All according to the specifications, drawings, and engineer's approval. The contractor should submit sample for approval from the Engineer before starting. The material used must have a valid quality certification from the Palestinian Institue for Standards and Measurements and pass all tests of paintings as conducted in authorized lab |  |  |  |  |  |  |
| 6.01 | Supply and paint emulsion paint (Supecryl) for internal existing walls ( two coats ) the item include removing the cracks of paint ,maintenance of painted areas, smoothing the walls, cleaning the surface very well in the areas where the supervisor engineer indicates to prepare it to new painting & all the required materials according to specifications and Engineer's instructions. |  | M2 | 400 |  |  |  |
| 6.02 | Supply & paint oil paint for and internal existing walls(two coats) the item include removing the cracks of paint, using putty in areas where cracks removed until having plain surface, smoothing the walls, cleaning the surface very well in the areas where the supervisor engineer indicates to prepare it to new painting ,the item including a pendrol layer before oil paint & all the required materials according to specifications and Engineer's instructions. |  | M2 | 250 |  |  |  |
| Total NIS |  |  |  |  |  |  |  |

# Section IV

Technical Specifications

Technical Specifications

3 STANDARDS	29

4 CONTRACT DOCUMENTS	29

4.1	Contract Drawings	29

4.2	Bill of Quantities and Bid Prices	29

4.3	Shop Drawings	30

4.4	“As-Built” Drawings	30

4.5	Inconsistency in Contract Documents	30

5	PROTECTION AND CONSERVATION OF THE WORKING ENVIRONMENT30

5.1	Precautions against Contamination of the Works	30

5.2	Archaeological Site and Artefacts	31

5.3	Suppression of Noise and Pollution	31

5.4	Site Cleanliness	31

5.5	Cleaning Up	32

5.6	Protection of Works	32

5.7	Operation of Existing Utilities	33

5.8	Location of Existing Subsurface Structures and Utilities	33

5.9	Other Construction Activities	34

6. ACCESSIBILITY TO WORKING SITE AND TRAFFIC REGULATION ……..34

6.1	Limits and Restrictions to Working Site	34

6.2	Access Roads	34

6.3	Restrictions on use of Roads	35

6.4	Site along Pipelines in Roads	35

6.5	Closing of Roads, Traffic Diversion and Control	36

7 SAFETY PROVISIONS	37

7.1	Safety and Accommodation for Contractor’s Staff	37

7.2	First Aid Outfits	37

7.3	Protective Equipment and Clothing	37

7.4	Safety of Adjoining Existing Buildings	37

8 - EARTHWORKS	38

8.1	Scope of Work	38

8.2	Site Preparation	38

8.3	Setting-Out	39

8.4	Excavation	39

8.5	Removal, Restoration and Maintenance of Surface	41

8.6	Trench Excavation	41

8.7	Excavation for Concrete Valve Chambers	43

8.8	Excavation for Concrete Blocks	44

8.9	Backfilling of Trenches	44

8.10  Backfilling around Structure	46

8.11	Material Used in Backfill	47

8.13	 Replacement of Pavements and Structures by the Contractor	48

8.14  	Road Crossing	49

10 CONCRET WORKS	51

10.1 CONCRETE AND REINFORCED CONCRETE WORK	51

10.1.1	General	51

10.1.1	Formwork for Concrete	52

10.1.2	Reinforcement for Concrete	53

10.1.3	Concreting	55

10.1.4	Construction of Manholes	65

Special Specifications	67

GEOMEMBRANE LINER	67

General

A	These Technical Specifications are given as a base line for the contractor to understand the minimum requirements of MoH for implementation of this contract.

## 3 	STANDARDS

A	The works have been designed to incorporate and utilize economically high quality product standards and workmanship to various specifications which are detailed herein.

B	Preference shall be given to ISO Standards (International Standards Organization) as described in the attached list of Products Standards.

C	Second priority shall be given to JSS (Jordan Standard Specifications) and IS (Israeli Standards). These shall be followed where described in this Technical Specifications and in the attached list of Product Standards.

D	Other standards such as EN (European Committee for Standardization /CEN), BS (British Standards   Institution / BSI), AFNOR (Association Francaise de normalization), DIN (Duetsches Standards fur Normung), ASTM (American Testing and Material Standards), ANSI (American National Standards Institute), ACI (American Concrete Institute), AWWA (American Water Works Association) can only be used either if they are compatible and better than the relevant ISO Standards or when an ISO Standard is not covering the product. Documentation for this is to be attached to tender.

E	All standards and references shall in every case be deemed to include the latest edition or issue of such standards.

## 4	CONTRACT DOCUMENTS

### 4.1	Contract Drawings

A	The approved detailed drawings will be prepared by the contractor and  shall be set-out in the Particular Conditions and Specifications together with all drawings which will be approved by the engineer.

B	All lines, elevations and measurements shown on the Drawings are only conceptual only. It shall be the Contractor’s responsibility through the contract to complete the detailed design and specifications.

### 4.2	Bill of Quantities and Bid Prices

- The contractor has to submit price analysis for all the work, and this will be after approval the base for any additional/omission works.

- It shall be the responsibility of the Contractor to satisfy himself as to the Correctness of the Quantities of materials to be supplied and amount of works to be carried out before submitting his bid price.

- The Contractor shall, after a thorough and careful study of all the required works comprised in the various sections of the several Documents of the Contract, make an assessment of the amount of all the works comprised and shall quote in the Bill of Quantities a Bid Price for each of the various items of Works described, which price  shall be binding subject to the relative Clauses of the Contract.

### 4.3	Shop Drawings

- The contractor shall provide at his own expense any number of shop drawings which, in the opinion of the Engineer, are necessary for the proper execution of a specified work. The Contractor shall not proceed with the above mentioned work unless these shop drawings are approved by the Engineer.

### “As-Built” Drawings

- All prints of the “Shop Drawings” , where required, shall be corrected by the Contractor and submitted to the Engineer for approval as the Works proceed. Upon the completion of the Works, the Contractor shall prepare a complete set of “As Built” Drawings for the project as executed, including tie-ins, presented on a computerized electronic form, and submit them to the Engineer for approval. When approved by the Engineer, the Contractor shall submit a digital copy on the specified format  for each project and six copies of all Drawings duly marked “As-Built”. The final payment shall not be made except for the actual Works that have been completed in accordance with the Specifications and have been duly presented on the  “As-Built” Drawings.

- The Contractor shall not be entitled to any extra payment or extension of time for the correction, preparation and supplying of the mentioned and transparencies.

### 4.5	Inconsistency in Contract Documents

A	The Contractor shall execute the Works according to the provisions of the approved detailed drawings, approved specifications and Contract Documents. In the event of any unforeseen or unintended conflict between the Particular Conditions and Specifications and this Specifications, the former shall prevail.

B	If the Contractor should discover that any work has been omitted and / or  not indicated entirely or partially from all the documents, but that such work is essential to the safety or proper functioning of the Works, he shall report the facts immediately to the Engineer. If the work is something which in the opinion of the Engineer could not have been foreseen by an experienced Contractor, the Engineer shall issue to the Contractor a variation order stipulating the details of the work to be done. Save as aforesaid in the above paragraph, no additional payment shall be made in respect of work carried out in connection with discrepancies between the various Contract Documents.

## 5	PROTECTION AND CONSERVATION OF THE WORKING ENVIRONMENT

### 5.1	Precautions against Contamination of the Works

A	The Contractor shall satisfy the Engineer that all his personnel working on the site are medically fit to be in contact with a public water supply and his personnel shall undergo any necessary medical test to show that they are free from any infectious diseases and are not carriers of any such diseases.

B	The Contractor shall at all times take every possible precaution against contamination of the Works. The Contractor shall give strict instructions to all persons employed by him to use the sanitary accommodation provided.

C	Throughout the Contract the Site and all Permanent and Temporary Works shall be kept in a clean, tidy and sanitary condition.

D	The Contractor shall at all times take measures to avoid contamination of existing water-courses and drains by petrol products or other harmful materials.

E	The Contractor shall be responsible for making all arrangements for the disposal of wastewater including the disposal of water from the water testing of mains on his own expense. He shall be responsible for obtaining permits from Local Governates prior to such disposals.

### 5.2	Archaeological Site and Artefacts

A	If, during construction, excavations reveal remains and artefacts of archaeological interest, the Contractor shall immediately inform the Engineer and abide by the Engineer’s directions, and shall coordinate and modify the sequence of the execution of the Work. It should be understood that the sole owner of the archaeological site and artefacts is the Palestinian National Authority.

### 5.3	Suppression of Noise and Pollution

- The Contractor shall make every reasonable endeavor both by means of temporary Works and by the use of particular plant or silencing devices to ensure that the level of noise or pollution resulting from the execution of the Works does not constitute a nuisance.

- The Contractor shall take all such precautions as may be necessary in the conduct of the work to avoid water pollution, air pollution, noise pollution harmful to health, spreading of plant diseases and pests or damage to natural resources or the environment, all as is consistent with good practice and as required by applicable laws, ordinances and regulations or lawful orders or authority having jurisdiction.

### 5.4	Site Cleanliness

A	The Contractor shall make every effort to keep his site in a clean and orderly manner. He shall not deposit his builders’ refuse indiscriminately but shall arrange for all waste to be transported to an authorized pit. He shall not deposit his refuse into trenches in backfilling.

B	Public highways services, streets, paved paths, passages, pavements, etc., must be kept clean and free of  spoil and rubbish and must be brushed and washed as required by the Engineer.

C	If the Contractor fails to keep his site clean after receiving the Engineer’s written warning notice, then the Engineer will instruct a third party to carry out the work and the costs shall be recovered from the Contractor through the Contract.

### 5.5	Cleaning Up

- On or before the completion of the work, the Contractor shall, unless otherwise especially directed or permitted in writing, tear down and remove all temporary buildings and structures built by him; shall remove all temporary Works, tools and machinery or other construction equipment furnished by him; shall remove, acceptably disinfect, and cover all organic matter and material containing organic matter and in, under and around privies, houses and other buildings used by him; shall remove all rubbish from any grounds which he has occupied and shall leave the roads and all parts of the premises and adjacent property affected by his operation in a neat and satisfactory condition.

- The Contractor shall restore or replace, when and as directed, any public or private property damaged by his work, equipment, or employees, to a condition at least equal to that existing immediately prior to the beginning of operations. To this end the Contractor shall do as required all necessary highway or driveway, walk and landscaping work. Suitable materials, equipment and methods shall be used for such restoration.

- The Contractor shall thoroughly clean all materials and equipment installed by him and his subcontractors and on completion of the work shall deliver it undamaged and in fresh and new appearing condition. All mechanical equipment shall be left fully charged with lubricant and ready for operation.

### 5.6	Protection of Works

- The Contractor shall take every care to prevent damages to the Works from whatever cause and shall ensure that adequate protection is given to all Works from activities of following trades and nominated Sub-Contractors.  Vulnerable parts of the Work particularly liable to damage, shall be protected as may be reasonable required by the Engineer’s Representative.

- The Contractor shall keep all persons (including those employed by Sub-Contractors) under control and within the boundaries of the Site.  He will be held responsible for the care of the existing premises and of the Works generally until their completion, including all work executed and materials, goods and plant (including those of sub-Contractors and suppliers) deposited on the Site; together with all risks arising from the weather, carelessness or of work people, damage or lost by theft or any other cause; and he shall make good at his own expense, all such damage and loss.

- The Contractor shall keep the Works well drained until the Engineer certifies that the whole of the Works is substantially complete and shall ensure that so far is practical, all Work is carried out in the dry weather.  Excavated areas shall be kept well drained and free from standing water.

- The Contractor shall construct, operate and maintain all temporary dams, watercourses and other Works of all kinds including pumping and well point de-watering plant that may be necessary to exclude water from the Works while construction is in progress.  Such temporary Works and plant shall not be removed without the approval of the Engineer’s Representative.

- Notwithstanding of any approval by the Engineer of the Contractor’s arrangements for the exclusion of water, the Contractor shall be responsible for the sufficiency thereof and for keeping the Work safe at all times particularly during any floods and/or making good at his own expense any damage to the Works including any that may be attributable to flood.  Any loss of production of additional costs of any kind that may result from floods shall be at the Contractor’s own risk.

### 5.7	Operation of Existing Utilities

A	The existing utilities must be kept in continuous operation throughout the construction period. No interruption will be permitted which adversely affects the level of service provided.

B	Provided permission is obtained from Employer and Engineer in advance, portions of the existing utilities may be taken out of service for short periods corresponding with periods of minimum service demands. Such permission will not relieve the Contractor of any of his responsibilities under the Contract.

### 5.8	Location of Existing Subsurface Structures and Utilities

- Before beginning excavation operations, the Contractor shall contact the specified Departments and Authorities and notify them of his intention to begin excavation operations.

- The Contract Drawings may show certain utility or other structures or facilities believed to exist in the working area, the exact location of which may vary from the locations indicated. All other structures or facilities may not be shown. The Drawings do not show all existing subsurface structures or utilities.

- It shall be the responsibility of the Contractor to determine the exact location of such pipeline, subsurface structures and / or utilities ahead of his Work by exploratory, excavation or other means and to take suitable precautions to prevent damage to them and to prevent interruption of the services which such facilities provide. If they are unintended broken or damaged, they shall be restored by the Contractor or the appropriate utility at the Contractor’s expense.

- The Contractor will be paid for all works necessary to complete exploration and relocation of subsurface and/or utilities by each linear meter of the measured pipeline.

- Where necessary, the Contractor shall use hand tools to excavate test pits prior to excavation to determine the exact locations of existing utilities. It shall be the responsibility of the Contractor to make such explorations sufficiently in advance of construction to enable the Engineer to approve modifications, if any, to be made to the pipeline, structure or conflicting utility. The Contractor shall obtain the permission of the Engineer before commencing any test pits and shall fence, mark and protect them, as required by the Engineer. Test pits shall be refilled by hand as soon as practicable after the necessary information has been obtained.

- As the excavation approaches sewers conduits, cables or other underground facilities, and with care the excavation shall be continued by means of hand tools. Where necessary, the Contractor shall provide temporary support for the existing utilities to prevent damage during his operations. Notwithstanding these provisions, if damage to existing utilities results from the Contractor’s operations, such damage shall be repaired without delay by the Contractor or such repairs shall be borne by the Contractor.

- If damage to existing utilities causes disruption to Contractor’s Schedule of Work by delaying Work in the area of such damage, the Contractor shall readjust his Schedule, methods of working and resources so that critical dates in the Schedule for the completion of the Contract are not affected.

- In case of pipelines, subsurface structures and /or utilities encountered in the work coincide with the pipe line route, the Engineer shall have the authority to change the plans and order a deviation from the line and grade, or arrange with the Employers of the existing structures for removal, relocation or reconstruction of the obstruction following the procedures of the Employer at the Contractor’s expense.

- If the change in plans results in change of the length of pipes to be executed by the Contractor, such altered work shall be done on the basis of payment to the Contractor for extra length or credit to the Employer for less work. This payment will be made for extra exploration and relocation of structures and utilities, pipes, valve chambers, excavation, backfilling and depth of line due to these changes.

Conditions of the Contract (please refer to CC clause 62.1)

### 5.9	Other Construction Activities

- The Contractor shall note that other works, might be constructed in the Site of Works. He shall co-operate with the construction of such works in organizing their respective contracts so as to cause minimum of interference to each other and to the public. No claims resulting from such co-operation shall be entertained by the employer except as stipulated in the Conditions of Contract.

## 6	ACCESSIBILITY TO WORKING SITE AND TRAFFIC REGULATION

### 6.1	Limits and Restrictions to Working Site

- Generally, working sites shall be confined by physical restrictions and the maintenance of accesses and traffic flow. The Contractor shall agree on the extent of his working areas with the concerned Authorities and the Engineer.

### 6.2	Access Roads

A	The Contractor shall construct and maintain such temporary access roads as he may require for carrying out the Works at his own expense.

B	Immediately after ceasing to use any of the temporary roads the Contractor shall restore the road to the satisfaction of the Engineer and the responsible Authority or Employer. The provision of this Sub-Clause shall apply also to the shoulders and verges of any existing sealed road used by the Contractor affected by his operations.

C	The Contractor shall at his own expense maintain and repair any damage caused to highways, streets and underground structures by his vehicles, irrespective of any protective measure taken.

### 6.3	Restrictions on use of Roads

A	The Contractor shall not run tracked vehicles or tracked plant on any public or private road without the written approval of the Engineer and the responsible Authority or Employer and subject to such conditions as each may require.

B	The Contractor shall observe all weight and dimension restrictions which apply to roads and tracks in Palestine and he shall comply with all reasonable restrictions which may from time to time be imposed by the Engineer, Employer, Police, Ministry of Public Works or responsible Authority.

### 6.4	Site along Pipelines in Roads

i) General

A	Without prejudice to the generality of the Conditions of Contract, the site along with pipelines in roads, unless the road is closed as hereafter provided, shall so far as possible be so limited that in all cases a free passage along such roads shall be maintained for vehicular traffic and pedestrians.

B	The Contractor shall provide access to all properties including garages fronting on such roads

C	The Contractor shall assume and have full responsibility for the adequacy of safety provisions on all streets, roads, private ways and walks affected by his work.

ii) Public Roads

A	Notwithstanding requirements stated elsewhere in the Specification, the Contractor shall comply with the additional requirements contained in this Clause whenever carrying out any work in connection with pipe laying in or adjacent to public roads.

B	The Contractor shall at all times carry out any work in or adjacent to public roads in manner to the approval of the Engineer and the competent Authorities and only at such times and during such hours as may be agreed by the competent Authority.

C	At no time shall the Contractor commence work in or adjacent to any public road without the prior approval of the Engineer.

D	The Contractor shall, when working in or adjacent to any public road, cause the least interference possible to the flow of traffic and shall at all times, maintain unimpeded sufficient width of the carriageway, at no time less than 3m, to permit single lane traffic.

E	The Contractor shall control the flow of traffic past restrictions caused by his operations by means of electrical controlled flashers positioned ahead of and behind the restricted section of heavy traffic road. The traffic lights shall be to the approval of the Engineer and be lit at all time and for as long any restrictions caused by the Contractor’s operations exist. Traffic lights shall be continuously attended by flag men and the time interval between light changes shall be capable of adjustment to suit varying patterns of traffic flow. Warning signs shall be posted well in advance of any section of restricted road.

F	All sections of roadway affected by the Contractor’s operations shall be bounded by barriers, tapes, bunting or similar means to afford adequate and effective warning, such as flagging, lighting, watching and traffic control to all road users. Such boundaries shall in addition be adequately lit by warning lanterns at all times during the hours of darkness.

G	The Contractor shall at no time string pipes on the carriageway of any public road.

H	The Contractor shall arrange his work in or adjacent to public roads in such a way that at no time the length of road restricted by his operations exceeds 100 meters in urban areas and 500 meters in rural areas.

### 6.5	Closing of Roads, Traffic Diversion and Control

i) Closing of Roads

A	The Contractor shall not close any road unless the Authority having charge of the road surfaces shall have previously given the appropriate notice or made the appropriate order and without the Contractor having first obtained the written consent of the Local Authority to close the same. In the event of such consent being refused, the Contractor shall have no claim for any additional payment. In the event of such consent being given, the Contractor shall provide, fix and maintain all warning signs and diversion notices as may be required by the said Authority and by the Engineer.

ii) Traffic Diversions

A	Traffic diversions shall be planned by the Contractor with the Engineer, the Traffic Section of the Public Works Directorate and the Traffic Directorate of the Ministry of  the Interior. No diversion shall be implemented without the written consent of the Engineer. Access to a closed road shall be made available to any vehicle of the emergency services.

iii) Traffic Signs

A	The Contractor shall provide, erect and maintain on the Site and such locations on the approaches to the Site, as may be required by the Traffic Directorate and / or the Engineer, all traffic signs and traffic control signals necessary for the safe direction and control of traffic. This shall apply whether the Site is in or immediately adjacent to the carriageway such that normal passage of traffic is affected.

B	The size of all such signs and the lettering thereon shall be approved by the Engineer before erection of the signs. All signs shall have directions written in both Arabic and English and shall carry direction arrows where appropriate. The signs shall be reflectorised or adequately illuminated by night in a manner approved by the Traffic Directorate and/or the Engineer and kept clean and legible at all times. The Contractor shall reposition, cover or remove signs as required during the progress of the Works.

C	Wherever single file traffic is necessary on a highway by reason of the construction of the Works, the Contractor shall provide and maintain a minimum carriageway width of 3 meters or wider where necessary as so instructed by the Engineer.

## 7	SAFETY PROVISIONS

### 7.1	Safety and Accommodation for Contractor’s Staff

A	The Contractor shall ensure that all safety and welfare measures required under or by virtue of the provisions of any enactment or regulation are strictly complied with.

B	The Contractor shall provide and maintain suitable and sufficient shelters and mess rooms for his workmen and supervisory staff as are customary and necessary.

C	The Contractor shall provide at all construction sites sufficient closets or latrines to comply with Government Regulations. They shall be properly screened and maintained in a clean and sanitary state at all times.

D	Camps for workmen, if provided, shall comply with all relevant Government Regulations and shall be laid out in an approved and orderly manner. Proper provision shall be made for the disposal of all waste and refuse, and there shall be an adequate supply of  water for washing, cooking and drinking purposes. Sleeping quarters shall be properly ventilated and lighted, and the whole camp shall be maintained and cleaned at all time to comply with Government Regulations.

### 7.2	First Aid Outfits

A	The Contractor shall provide and maintain for the duration of the Contract adequate first aid outfits at each construction site. The Contractor shall provide for the transport of serious cases to nearest hospital.

### 7.3	Protective Equipment and Clothing

- The Contractor shall provide and maintain all necessary protective and safety equipment and clothing for the operative and Site staff.

### 7.4	Safety of Adjoining Existing Buildings

- The Contractor shall take all necessary precautions during the excavation for the Works particularity those excavations which are adjoining existing building and shall protect such buildings from damage or collapse by means of temporary or permanent shoring, strutting, sheet piling or underpinning or excavation in short length and/or other methods as he deems fit. Also, he shall properly support all foundations, trenches, walls, floors, etc., affecting the safety of the adjoining existing buildings.

- The Contractor shall alter, adopt and maintain all such Works described above for the whole period of the Contract and shall finally clear away and make good all damages done.

- The construction and efficiency of the shoring, underpinning, strutting, etc. ... , for the purpose for which it is erected shall be the responsibility of the Contractor. Should any subsidence or any other damage occur due to the inefficiency of the shoring, underpinning, strutting, etc. , or any other support provided, the damage shall be repaired by the Contractor at his own expense and responsibility.

- The shoring, strutting, piling, etc. , shall be executed in such a manner as to cause as little inconvenience as possible to adjoining Employers or the public and the Contractor shall be responsible for negotiating with the adjoining Employers the means to safeguard their property and for the use of any portion of their land for the purpose of executing the excavations and no claims submitted on this ground will be entertained.

- The Contractor shall be held solely responsible for the safety of the adjoining existing buildings, the sufficiency of all temporary or permanent shoring, underpinning, strutting, piling, etc.,

- The Contractor shall keep the Engineer informed as to the manner in which he intends to proceed with the execution of the excavations, submit his proposed methods of shoring, etc., and obtain his approval, such approval if given shall not absolve the Contractor of his responsibility under this clause.

- The Contractor shall save harmless and indemnify the Employer in respect of all claims, demands, proceedings, damages, costs, charges and expenses whatsoever arising out of or in relation to any such matters in so far as the Contractor is responsible under this clause.

## 8 - EARTHWORKS

### 8.1	Scope of Work

- This section covers trenching and backfilling work and shall include the necessary clearing, grubbing and preparation of the site; removal and disposal of all debris; excavation and trenching as required; the handling, storage, transportation and disposal of all excavated material; all necessary sheeting, shoring and protection work; preparation of subgrades; pumping and dewatering as necessary or required; protection of adjacent property;  pipe embedment; surfacing and grading; and other related work.

### 8.2	Site Preparation

- Prior to commencing any excavation work, the Contractor shall establish a horizontal and vertical survey, record existing ground elevations and stake the location of trenches to be excavated.

- The Contractor shall prepare the site for construction by clearing, removing and disposing of all items not indicated on the Drawings to remain or so defined by the Engineer.

- The Contractor shall obtain relevant excavation and road cutting permits as required to commencing work.

i) Existing Subsurface Structures and Utilities

- For all works required to deal with existing subsurfaces and utilities refer to General Section of these Specifications.

ii) Clearing, Grubbing and Grading

- The Contractor shall perform the clearing and grubbing (if any), of top soil consisting mainly of loose soil, vegetable and organic matters, drift sand, unsuitable soil and rubbish by scarifying the areas to be excavated and sidewalks to a minimum depth of 300 mm from the natural ground level. All materials resulting from the above operations shall be removed from the site, loaded and transported and off loaded, spread and levelled to approved dumps as directed by the Engineer.

- The Contractor shall include for grading the route to provide access for his equipment and personnel, executing all cuttings to remove the high point of rises in terrain and in all respects prepare the route for pipe laying operations, all in accordance with the requirements of good pipeline construction practice.

### 8.3	Setting-Out

- The Contractor shall stake-out the work as shown on the Drawings and secure the Engineer’s approval of his stake-out before proceeding with construction. If, in the opinion of the Engineer, modification of the line or grade is advisable before or after stake-out, the Engineer will issue detailed instructions in writing to the Contractor for such modification and the Contractor shall revise the stake-out for further approval in accordance with the relevant Clause of the Conditions of Contract.

### 8.4	Excavation

A	The Contractor shall perform all excavation true to lines, widths and depths shown on the Drawings or to such further lines, depths or dimensions as may be directed by the Engineer.

B	Excavation work will be classified according to the quality of the material to be excavated. In three classes as follows

- Excavation in Rock

- Excavation in sand

- Excavation in mixed soil

C	The soil classes in every section of the pipeline will, if necessary, be determined by the engineer on the basis of the following definitions:

D 		Excavation in Rock shall include the removal of hard and solid rock in continuous layers or boulders that cannot be broken up by ordinary excavating equipment including rooter, and which necessitate the use of  pneumatic tools or wedges for loosening and removal.

E 		Excavation in Sand shall include excavation in loose or dense sand , such as drifting sand(dunes).

F		Excavation in mixed soil shall include the removal of all material that cannot be classified as rock or sand as defined above(Heterogenuous Soil).

G		Everything said in the specification with regard to the execution of excavations, disposal of excavated materials,  etc.  shall equally apply to rock, sand and common excavation, unless otherwise stated.

i) Road along the line .

- Wherever necessary the Contractor shall prepare a road along the line at such distance from the line that the traffic on the road will in no way interfere with pipelaying work.  The Contractor shall also prepare access roads from the highway or other public roads to the said access road.

- The road along the line and the access roads  shall permit the normal movement of  trucks and other vehicles and all equipment and plant required for the execution of the works.

- The employer’s employees shall at times have the use of the roads prepared by the Contractor, free of charge.

- The Contractor shall maintain the road along the line and the access roads in a good and serviceable condition and shall make all repairs that may be necessary during the whole period of construction.

ii) Excavation to reduce levels.

- Wherever shown on the drawings, the Contractor shall reduce the ground level on the trench site,  prior to commencement of trench excavation.  Before starting excavation for reducing of levels the Contractor shall move the marking of the alignment to such a distance that the marks will not be destroyed and will not interfere with the execution of the work.

- Excavation for reducing levels shall be done to the lines and levels shown on the drawings.  Where the depth of excavation is not so shown it shall be done to a line parallel to the trench bottom in the section concerned.

iii) Storing of Suitable Excavated Material

- During excavation, materials suitable for backfill and fill will be stockpiled on the site at sufficient distance from the sides of the excavation to avoid over-loading and prevent cave-ins or mixing with the concrete during the construction of  foundation.

iv)  Disposal of Unsuitable and Surplus Excavated Material

- Upon the order of the Engineer, all unsuitable and surplus materials shall be immediately removed, loaded and transported off the Site area by the Contractor to approved dumps and he shall abide by the relevant local regulations.

v) Unauthorized Excavation

- If the bottom of any excavation is taken out beyond the limits indicated or prescribed, the resulting void shall be backfilled by well graded material at the Contractor’s expense with thoroughly compacted to an acceptable proctor as directed by the Engineer,  if the excavations are for a structure or a manhole , then the void should be filled by class B150 concrete.

### 8.5	Removal, Restoration and Maintenance of Surface

i) Removal, Cut of Pavement

- The Contractor shall remove/cut pavement or concrete and road surfaces as a part of the trench excavation, and the amount removed shall depend upon the width of trench specified for the installation of the pipe and the width and length of the pavement area required to be removed for the installation of valves, fittings, valve chambers, thrust blocks, manholes, or other structures. The width of pavement removed along the normal trench for the installation of the pipe shall not exceed the top width of the trench specified by more than 200 mm on each side of the trench. The widths and lengths of the area of pavement removed for the installation of pipes, valves, fittings, valve chambers, thrust blocks, manholes, or other structures shall not exceed the maximum linear dimensions of such structures by more than 300 mm on each side. Wherever, in the opinion of the Engineer, existing conditions make it necessary or advisable to remove additional pavement, the Contractor shall remove it as directed by the Engineer but shall receive no extra compensation therefore. The Contractor shall use such methods, either drilling or chipping, as will assure the breaking of the pavement along straight lines. The cut must be sharp and approximately vertical.  The Engineer’s representative may require that the pavement be cut with asphalt cut machine without extra compensation to the Contractor.

ii) Restoration of Damaged Surfaces and Property

- If any pavement, trees, shrubbery, fences, poles, or other property and surface structures have been damaged, removed, or disturbed by the Contractor, whether deliberately or through failure to carry out the requirements of the contract documents, state laws, municipal ordinances, or the specific direction of the Engineer or through failure to employ usual and reasonable safeguards, such property and surface structures shall be replaced or repaired at the expense of the Contractor. If the Employer specifies that the replacements or repairs shall be made by the Contractor, he shall replace or repair and restore the structures to a condition equal to that before the work began and to the approval of the Engineer and shall furnish all incidental labour and materials.

### 8.6	Trench Excavation

- General

- The minimum trench width at the bottom shall be equal to the external pipe diameter plus 500 mm provided that the minimum clearance between the installed pipe and the trench side shall not be less than  250 mm.  The rest of the trench, unless otherwise shown on the drawings or instructed by the Engineer, shall be excavated with approximately vertical sides as much as possible.

- The trench width at the ground surface shall be excavated as narrow as practicable but may vary with , and depend upon its depth and the nature of the ground encountered.

- Trenches shall be of such extra width, when required, as will permit the convenient placing of timber support, sheeting and bracing and handling of specials.

- The graded material  bedding under the pipe shall be not less than 150 mm thick  in any point and as shown on the drawings and as directed by the Engineer.

- The trench depth shall give the required minimum cover over the pipe as specified.

- The trench bottom shall be straight and even so as to provide a good support for the pipe on its entire length and shall be free of roots, stones, lumps and other hard objects that may injure the pipe or its coating.  The excavated material shall be placed alongside the trench in such a manner as not to interfere with the work and to prevent its falling down into the trench.

- Where welds or joints of pipes and accessories are required to be done in the trench, it shall be widened or deepened to the usual enlarged dimensions or as directed by the Engineer so as to easily permit the proper execution of all welding and fixing works at all their stages, coating repairs, and thorough inspection of all these operations.

- Separate excavations are to be made for manholes, pipe junctions, etc.

ii) Types of Trench Excavation

- Common and Sand Excavation.

- When excavating in ordinary soil or sand the Contractor shall take all precautions to prevent slides caused by material placed alongside the trench or for any other reason.

Wherever the danger of slides exists, the Contractor shall slope the trench walls, install supports, bracing, etc. , and shall make all other arrangements which may be necessary to prevent slides.

- Trench Excavation in Rock.

- Trench walls excavated in rock shall be as nearly vertical as possible, and the Contractor shall consolidate the walls wherever they have been  loosened by blasting or for other reasons, or shall remove the loosened material.

- Trench Excavation in water.

- Where rivers carrying water during construction are to be crossed, the Contractor will have to excavate the pipe trench under water.  The depth and width of the trench at such places shall be as specified above.  The exact trench profile at river crossing will be shown on drawings or determined by the Engineer on the site.  The Contractor shall take all necessary measures to maintain the trench in its proper shape and to prevent it from being filled with eroded earth or mud until the pipe has been laid.

- Mechanical Excavation

- The use of mechanical equipment must be jointed with the approval of the Engineer. The use of mechanical equipment will not be permitted in locations where its operation would cause damage to trees, buildings, culverts or other existing property, utilities or structures above or below ground. In all such locations hand excavation shall be used. The Contractor will be held responsible for making good at his own cost all additional damage to road surfaces and private lands caused by the use of mechanical excavators.

- Mechanical equipment if used for trench excavation shall be of type approved by the Engineer. Equipment shall be so operated that the rough trench excavation bottom can be controlled, that uniform trench widths and vertical sides are obtained at least from an elevation 200mm above the top of the installed pipe when accurately laid to specified alignment will be centered in the trench with adequate clearance between the pipe and sides of the trench.

- Alignment and Minimum Cover

- The alignment of each pipeline shall be fixed and determined from offset stakes. Horizontal alignment of pipes and the maximum joint deflection used in connection therewith shall be in conformity with requirements of the section covering installation of pipe.

- Pipe grades or elevations are not definitely fixed by the Contract Drawings, trenches shall be excavated to a depth sufficient to provide a minimum depth of backfill cover over the top of the pipe of 900mm for diameters 150mm and above, 700mm for diameters less than 150mm or as mentioned in the bill of quantities. Greater pipe cover depths may be necessary at certain locations, the locations and depths will be determined by the Engineer, and will be followed by the Contractor. Measurement of pipe cover depth shall be made vertically from the outside top of pipe to finish ground or pavement surface elevation except where future surface elevations are indicated on the Drawings. Where there is no adequate minimum cover, concrete encasement will be used as hereinafter and as shown on the Drawings and as directed by the Engineer.

- Excavation in Confined Areas.

- In confined areas, where the passage of excavating equipment is impossible, or where the Engineer deems to use of such equipment impracticable or undesirable for any reason whatsoever, trench excavation shall be done by hand.  All requirements specified above for common or sand excavation shall also apply to trench excavation by hand.

- Padding of Trench Bottom.

- Wherever the trench bottom is in rock or where the Engineer will decide that the trench bottom is unsuited for laying of pipe on it, the trench will be excavated to an additional depth, and the Contractor shall pad the trench bottom with a layer 100 mm thick of selected excavated material not containing stones larger than 30 mm measured in any direction provided that the quantity of stones smaller than 30 mm is not more than 20% by volume.

- The surface of the padding shall be finished to grade as specified above so as to provide an even and solid support for the pipes to be laid.

### 8.7	Excavation for Concrete Valve Chambers

- Excavation for the concrete valve chambers shall be carried out to the dimensions, lines and grades shown on the Drawings or required by the Engineer.

- Wherever the depth of the excavation or the nature of the soil makes it necessary to avoid caving in, the Contractor shall excavate the walls to a slope or brace and support the excavation.

- Should nevertheless earth slides occur, the Contractor shall remove the material resulting therefrom, clean the excavation of all stones, clods and other loose material and shall provide a clean excavation surface in which concrete can be cast according to the required dimensions and grades.

- Should it appear that the bottom of the excavation does not provide a solid base for the casting of the concrete floor, the Contractor will be required to consolidate the bottom using hand tampers and increasing the moisture content, if required, until the required density is obtained, a/o placing concrete class (B150) as blinding, all as directed by the Engineer.

- Any over-excavation at the bottom of the structure shall be restored to the proper grade by filling the over-excavation class (B150) concrete or shall be filled with the concrete of which the structure is cast. In the case of over-excavation in the walls, whether caused by careless work or by the necessity to prevent slides by excavating to a slope or for any other reason, the Contractor shall remove all loose material from the excavation, cast the walls of the structure to the dimensions shown on the Drawings and fill the spaces between the structures and the sides of the excavation with compacted backfill in layers of 100mm thickness. The material of the backfill shall be moistened if necessary and compacted to the level of the adjacent natural soil.

### 8.8	Excavation for Concrete Blocks

- Excavation for concrete anchoring blocks shall be performed according to the shapes and dimensions shown on the drawings.  The bottom and sides of the excavation shall be smooth, even, and solid so that concrete can be cast against them.  Wherever necessary, such surfaces shall be moistened and consolidated to make them suitable for the casting of concrete against them.  Any over excavation on the bottom or sides shall be cleaned, smoothened out, and filled with concrete cast integrally with block.

- After the block has been cast, and subject to the Engineer’s approval, it shall be covered where necessary with excavated material up to the natural ground surface.  The rest of the excavated material shall be removed and dump as specified above for the material excavated for valve chambers.

### 8.9	Backfilling of Trenches

- General

- Every section of the pipeline shall be covered as soon as possible after being lowered into trench, but no section of the line shall be covered without express approval of the Engineer.  Each section shall be backfilled after the pipe has been placed in its final position on the trench bottom and after all weld joints and bends have been coated and all defects in the pipe coating repaired.

- Backfilling shall be done carefully to prevent displacement of the pipe or injury to the pipes and their coating. The backfill material shall completely fill the entire space between the pipe and the trench surfaces, without leaving any voids.

- Care shall be taken that the backfill material does not contain any electrodes, scrap iron, fragments of timber or shrubs, roots, broken skids, tyres, ashes, refuse, oil or soil soaked with oil.  Stones removed during trench excavation may be used in the second stage of backfilling as specified below.

- On hillsides or sloping ground, furrows or terraces shall be provided across the pipeline trench to direct the flow of rainwater into the natural drain courses and away from the pipeline trench.

- Where the pipeline crosses natural drainage channels, an opening in the backfill shall be made to avoid interference with normal drainage of the surrounding land.

- Backfilling shall be done so as not to spoil the road or disrupt its continuity.

- Backfilling of Trenches in Cross-Country Areas

Where the pipes are laid cross-country, the backfilling of trenches shall be done as follows:

- Soft Backfill (surrounding the pipe) shall consist of sand from any approved source or fine aggregates. This

- material shall be placed 150 mm below the invert level up to 200 mm over the crown of the pipe and for

- the full width of the trench,  or to the depths specified in the Bill of Quantities.

- Final Backfill for the remainder of the trench shall be by using well graded approved backfill material. (as specified herein after in paragraphs 2.11( i , ii ))

- The trench shall be filled to the level of the natural adjacent ground level in layers not exceeding 300 mm, wetted and compacted by rolling, tamping to 90 percent  of maximum dry density.  If rolling is employed, it shall be by use of a suitable roller or tractor, being careful to compact the fill throughout the full width of the trench.

- Other layer of the same material shall be mounded 150 mm above the existing grade or as directed by the Engineer.

- Backfilling of Trenches in or Adjacent to Streets

Where the pipes are laid in or adjacent to streets, the backfilling of trenches shall be done as follows:

- Soft Backfill  shall be done as specified above in paragraph 2.9(ii-A)

- Final Backfill for the remainder of the trench shall be by using well graded approved backfill material. (as specified herein after in paragraphs 2.11( i , ii ))

- The selected backfill shall be up evenly on all sides, in layers not exceeding 250 mm measured before compaction, thoroughly wetted and compacted by rolling, tamping, or vibrating with mechanical compacting suitable equipment or hand tamping, to 95 percent of maximum dry density.  Where these methods are not practicable, compaction shall be done by using of pneumatic ramming with tools weighing at least 10 Kg. The materials in this case being spread and compacted in layers not more than 150 mm in thickness.  If necessary, sprinkling shall be employed in conjunction with ramming.

- The top 250mm sub-base for pavement replacement, shall consist of one layer of approved base course material, wetted and compacted to 95 percent of maximum dry density.

- Should the contractor wish to use the material excavated from the trench as sub-base for pavement replacement, the contractor shall at his own expense have samples of  the material tested by an independent and certified laboratory at intervals not to exceed 150 m, in order to establish its compliance with the specifications.  Only material which has been tested by the contractor and approved by the engineer shall be allowed to be incorporated into the work.

- Backfilling of Trenches with Excessive Slopes

- On trenches with slopes exceeding 15 percent, a 300 mm wide, stone partitions shall be built across the trench every 10 meters length.

- These partitions shall be done constructed over the first stage of the backfill up to the natural ground level, and shall exceed the trench width with 200 mm from each side inside the ground.

- The second backfill stage of the trench between the stone partitions shall be done as specified above.

- Restoring Trench Surface

- Where the trench occurs adjacent to paved streets, in shoulders, sidewalks, or in cross-country areas, the contractor shall thoroughly consolidate the backfill and shall maintain the surface as the work progress.  If settlement takes place, he shall immediately deposit additional fill to restore the level of the ground.  In some areas it  may be necessary to remove excess materials during the clean-up process, so that the ground may be restored to its original level and condition.

- The surface of any driveway or any other area which is disturbed by the trench excavation and which is not a part of the paved road shall be restored by the contractor to a condition at least equal to that existing before work began.

- Where the pipes are laid in cross-country areas, and where the danger of erosion exists, the uppermost 300 mm part of the trench may be backfilled with common backfill material containing fragments of ledge and boulders smaller than 150 mm providing that the quantity in the opinion of the engineer, is not excessive.  Small stones and rocks shall be placed in thin layers alternating with earth to insure that all voids are completely filled.

- All road surfaces shall be broomed and hose-cleaned immediately after backfilling.  Dust control measures shall be employed at all times.

### 8.10  Backfilling around Structure

- General

- Surfaces to receive backfill shall be cleared of debris and unsatisfactory materials prior to the placement of   the backfill material

- When the top 200mm of surface to receive backfill has a density less than the required maximum dry density,  break up surface, pulverize, moisten and compact such that the required degree of compaction is achieved to form a “compacted subgrade”.

- Backfill excavations as promptly as the work permits, but not until completion of inspection, testing, approval, and recording of location of underground utilities, as required.

- Backfilling - Common Fill

- Common Fill may be used as fill against exterior walls of structure as indicated on the  drawings.  Materials  conforming to the requirements of common backfill shall be placed in a layers having a maximum thickness of 300  mm measured before compaction, each layer of fill or backfill shall be moistened or aerated and compacted to at least     90 percent of maximum dry density, or as specified in the Bill of Quantities.

- Backfill or fill materials shall not be placed on surfaces that contain excessive moister, preventing specified degree  of compaction.

- Material placed in fill areas shall be deposited to the lines and grades shown on the drawings making due allowance for settlement of the material.

- No compacting shall be done when the material is too wet either from rain or from excess application of water.  At such cases, work shall be suspended until previously placed and new materials have dried sufficiently to permit proper compaction.

- Backfilling - Structural Fill

A	Structural fill shall be placed in layers having a maximum thickness of 200 mm in open areas and 150 mm in confined areas including points where conduit and piping join structures, measured before compaction.  Each layer shall be moistened or aerated and compacted to at least 95 percent   of maximum dry density, or as specified in the Bill of Quantities, by methods approved by the Engineer.  The limits of structural fill adjacent to structures shall extend as shown on the drawings.

B	Compaction of Structural fill in open areas shall consist of fuilly loaded ten-wheel trucks, a tractor dozer weighing at least 13.5 ton and operated at full speed, a heavy vibratory roller, or any method approved by the Engineer.

C	Compaction of structural fill in confined areas shall be accomplished by hand operated vibratory equipment or mechanical tampers approved by the Engineer.

### 8.11	Material Used in Backfill

- General

- Backfill and fill material shall be suitable excavated material, natural or processed mineral soils obtained from off-site sources, or graded crushed stones or gravel.

- Backfill and fill material shall be free from all organic material, trash, snow, ice, frozen soil, or other objectionable material which can’t be properly compacted.  Soft, wet, plastic soils which may be expensive, clay soils having a natural in-place water content in excess of 30 percent, soil containing more than 5 percent(by weight) fibrous organic material, and soil having a plasticity index greater than 30 shall be considered unsuitable for use as backfill and fill material.

- Backfill and fill material shall have a maximum of one percent expansion when testing is performed on a sample remolded to 95 percent of maximum dry density at a two percent below optimum moisture content under a 490 kg/m2 surcharge.

- Common Backfill Material

- Common Backfill or fill material shall not contain Granite blocks, broken concrete, masonry rubble, asphalt pavement, or any material larger than 150 mm in any dimension provided that this material is not more than 25 percent of the backfill or fill material.

- Common Fill shall have physical properties, as approved by the engineer, such that it can be readily spread and compacted.

- Selected Backfill Material

- Selected Backfill and Fill material shall conform to the requirements of common Backfill except that the material shall not contain any materials larger than 50 mm in its largest dimension provided that this material is not more than 20 percent of the Backfill or fill material.

- Structural Fill

- Structural Fill shall be gravel, sandy gravel, or gravelly sand.  Material shall have a plasticity index of less than 15 and shall conform to the gradation limits shown in table 2.1 below :

Table 2.1

| Sieve Size | Percent Finer By Weight |
| --- | --- |
| 150 mm | 100 |
| No. 4 | 20 - 70 |
| No. 40 | 5 - 35 |
| No. 200 | 0 - 7 |

- Crushed Stones

- Crushed stones shall be sound, durable stone, angular in shape, and free of foreign material, structural defects and chemical decay.  Crushed stones shall be of a maximum dimension of 50 mm and in a minimum of 12 mm measured in any direction.

### 8.13	 Replacement of Pavements and Structures by the Contractor

- Unless otherwise shown on the Drawings or mentioned in the bill of quantities, the Contractor shall restore all pavements, sidewalls, sidewalks, curbs, gutters, shrubbery, fences, poles, sod, or other property and surface structures removed or disturbed as a part of the work to a condition equal to that before the work began, and shall furnish all incidental Labour and materials. No permanent pavement shall be restored unless and until, in the opinion of the Engineer, the condition of the backfill is such as to properly support the pavement and not before written approval from the Engineer to commence such works.

- Where pipelines pass underneath asphalted roads and parallel to the axis of the road, the final 250 mm of the trench backfill  shall be furnished as follows:

- 200 mm (after compaction) shall be done by using  approved base course material, placed, wetted and

- compacted to not less than 95 % of the modified Proctor density.

- Spraying 2 kg of prime coat(MCO) per each square meter over the compacted base course,

and applying a layer of asphalt mix of size ¾  , in a thickness not less than 50 mm, after

compaction which should satisfy the specification of Palestinian Ministry of Public Works.

### 8.14  	Road Crossing

- Where water pipeline is crossing main roads, highways, or railways, the pipeline shall be installed inside a protective steel sleeve.

- Skids must be used to prevent damage to the pipe coating and to provide proper long-term line support.

- The water pipeline should not rest on the sleeve, skids should properly position the pipeline in the sleeve.

- Skids may extend for full length of the pipe with the exception of joint to be welded, or may be spaced at intervals. Skids must provide sufficient height to permit clearance between the pipe and the sleeve wall. Skids should be fastened securely to pipe with strapping, cables, or clamps.

- Table 2.2 specifies sleeve size requirements for wall thickness and maximum skid support spacing for water pipes of various diameters.

Table2.2- of Sleeve sizes

| Normal pipe size outside dia | Sleeve |  | Maximum skid support spacing |
| --- | --- | --- | --- |
| (in) | Outside dia ( in) | Minimum wall thickness (in) | (m) |
| 3 | 8 | 5/32 | 1.5 |
| 4 | 8 | 5/32 | 1.5 |
| 6 | 10 | 3/16 | 2.0 |
| 8 | 12 | 3/16 | 2.5 |
| 10 | 14 | 3/16 | 2.5 |
| 12 | 16 | 1/4 | 3.0 |
| 14 | 18 | 1/4 | 3.0 |
| 16 | 20 | 1/4 | 3.0 |

- Upon completion of pipe insertion, cast in place concrete B-150 shall  be used to restore the ground level  to 50 mm less than the previous asphalt level grade.

- After the concrete surface is dry,  the asphalt is reinstated  by spraying  0.5 kg of tack coat per each square meter prior to laying a 50 mm asphalt mix that satisfies the specifications of the Palestinian  Ministry Of  Public Works over the concrete surface.

- The ends of the sleeve shall be protected by casting concrete blocks B-150 for its full diameter and 150 mm thickness.

- Insulating Casing Spacers

Where the pipe crosses another pipe which is catholically protected the new pipes shall be installed inside a casing to electrically isolate the pipes from each other. To ensure the electrical isolation, modular insulating casing spacers shall be installed instead of the wooden kids as previously specified. The modular, insulating casing  spacers shall be bolt-on devices which fully encircle the pipe and are to be fabricated from stainless steel encirclement bands with pre-molded, insulating plastic skids.  Modular casing spacers shall be as manufactured by Cascade, PSI, or equal.

# CONCRET WORKS

## CONCRETE AND REINFORCED CONCRETE WORK

### General

British Standards (BS) Documents refered to in this section are:

BS EN 197-1:2000 Composition, specifications and conformity criteria for common cements.

BS 410 Test sieves. Technical requirements and testing.

BS 410-1:2000 Test sieves of metal wire cloth.

BS 410-2:2000 Test sieves of perforated metal plate.

BS 812-101:1984 (2000) Guide to sampling and testing aggregates.

BS 812-2:1995/BS EN 1097-3:1998

BS 812-100:1990 (1995)

BS 812-2:1995/BS EN 1097-3:1998

BS 812-100:1990 (1995)

BS 812-102:1989

BS 812-103.1:1985 (2000)

BS 812-103.2:1989 (2000)

BS 812-103´4:1994 (2000)

BS 812-105.1:1989 (2000)

BS 812-105.2:1990 (2000)

BS 812-106:1985 (2000)

BS 812-109:1990 (2000)

BS 812-110:1990 (2000)

BS 812-111:1990 (2000)

BS 812-112:1990 (1995)

BS 812-11:1990 (1995)

BS 812-113:1990 (1995)

BS 812-114:1989 (2000)

BS 812-117:1988 (2000)

BS 812-118:1988 (2000)

BS 812-119:1985 (2000)

BS 812-120:1989 (1995)

BS 812-121:1989 (2000)

BS 812-123:1999

BS 812-124:1989

BS 882:1992 Specification for aggregates from natural sources for concrete.

BS EN 1097-5:1999 Determination Of The Water Content By Drying In A Ventilated Oven

BS EN 1097-2:1998 Methods Of The Determination Of Resistence To Fragmentation

BS EN 1097-8:2000 Determination Of The Polished Stone Value

BS 4449 :1997 Specification for carbon steel bars for the reinforcement of concrete.

BS EN 12350-1:2000 Testing Fresh Concrete

BS EN 12350-2:2000 Testing Fresh Concrete

BS EN 12390-1:2000 Shape, Dimensions And Other Requirements For Speciament & Moulds

BS EN 12390-2:2000 Making And Curing Specimens For Strenght Test

BS EN 12390-3:2002 Compresenve Strength Of Test Specimens

BS EN 12504-1:2000 Cored Specimens. Taking, Examining And Testing In Compression

BS EN 12504-2:2001 Non Destructive Testing. Determination Of Rebound Number

The All materials shall be subject to such tests as the Project Manager may direct and provision for such tests shall be included in the price for such materials inserted in the Bill of Quantities or Schedule of Rates unless otherwise provided for.

Properly representative samples of all materials to be used in the works shall be submitted by the Contractor for the Project Manager's approval when required.

Where tests are required by the Project Manager, the Contractor shall take samples and send to a firm experienced in analysis of the material. Reports shall be submitted to the Project Manager. The Contractor shall bear all expenses consequent to the provision, taking and cartage, etc. of samples,in addition to the costs of performing the tests &reporting the results.

The Project Manager reserves the right to reject any material which, in his opinion is objectionable in any respect, not withstanding its apparent compliance with the relevant Standards. Any such rejected material shall be removed from the site at the Contractor's expense at once.

    - Formwork for Concrete

The Contractor shall supply, design, erect, strike and remove the formwork and be entirely responsible for its stability and safety so that it will carry the fresh concrete and all incidental loadings and preserve it from damage and distortion during its placing, vibration, ramming, setting and curing. It shall be so constructed as to leave the finished concrete to the dimensions shown on the Drawings and of a material capable of providing the surface finish specified. In any event, the maximum permissible deflection under all loads shall not exceed 2mm or 1/600 of the free span, whichever is less.

Formwork shall be of new timber and / or metal and shall include all temporary concrete moulds and their supports. Bolts to be used for fixing the formwork shall be approved by the Project Manager before staring the work.

For concrete surfaces which are to remain exposed wrought formwork shall be used. Wrought formwork shall be of timber or steel framing lined with 12mm thick smooth-faced plywood or an equal lining approved by the Project Manager, or of metal, suitable to obtain a fair face finish on the concrete. All external angles or fair faced in-situ concrete shall have chamfers formed with 15x15mm (5/8"x5/8") wrought hardwood angle fillets planted in the angles of the formwork, unless larger chamfers are shown on the drawings.

Formwork ready to receive concrete shall be thoroughly clean and the internal faces properly painted with an approved shutter oil or other preparation. Joints shall be tight to prevent leakage.

Wherever required and prior to placing of the reinforcement the internal surfaces of all formwork shall be treated with an approved mould oil.

All formwork shall be inspected and approved by the Project Manager prior to concreting. This approval, however, does not relieve the Contractor of any of his responsibilities.

The striking of all formwork shall be carried out with the greatest of care to avoid damage to concrete.

The formwork to vertical surfaces such as walls, columns and sides of beams may be removed in accordance with the table below although care must be taken to avoid damage to the concrete, especially to arrisses and features.

Minimum periods for striking other formwork should be in accordance with the following table, or as directed by the Project Manager Ordinary Portland Cement Concrete

Slabs (props left under) 					3 days

Beam soffits (props left under) 				7 days

Props to slabs 						 	7 days

Props to beams 						16 days

Vertical surfaces as walls, columns and sides of beams 	1 day

Formwork, shuttering, props, or any other means of temporary or semi-permanent support shall not be removed from the concrete until the concrete is sufficiently strong to carry safely the load (dead and temporary).

The Contractor shall inform the Project Manager when he is ready to strike the formwork, or remove any form of temporary support, and shall obtain his written consent before proceeding.

The times given for the removal of props are based on the assumption that the total live plus dead weight to be supported at the time of removal is not more than one half of the total design load.

For horizontal members where the loading is to be a higher proportion of the total design load these times may need to be increased.

The Contractor shall be responsible for any damage to the concrete work caused by or arising from the removal and striking of the forms and supports Any advice, permission or approval by the Project

Manager relative to the removal and striking of forms and supports shall not relieve the Contractor from this responsibility.

Any work showing signs of damage through premature loading is to be entirely reconstructed at the Contractor's expense.

The Contractor shall confirm positions and details of all

(a) permanent fixings

(b) pipes and conduit

(c) holes and chases

to ensure that alterations are not made without the knowledge and approval of the Project Manager.

The Contractor shall fix inserts or box out as required to correct positions before placing concrete, and shall form all holes and chases. He shall not cut hardened concrete without approval.

    - Reinforcement for Concrete

Steel reinforcement shall generally be hot rolled mild, medium or high yield steel smooth round or deformed bars complying with BS 4449 or similar approved standard .

In case any other type of reinforcement is required, it shall comply with the requirements of the BOQ and drawings.

All reinforcement shall be free from rust and mill scale and any coating such as oil, clay, paint etc which might impair the bond with the concrete.

Manufacturer's test certificates for all classes of reinforcement shall be supplied when required. Specimens sufficient for three tensile tests and three cold-bending tests per ten tons of bars or fraction thereof and for each different size of bar shall be sampled under the supervision of the Project Manager. Testing shall be in accordance with BS 4449 or other approved standard and batches shall be rejected if the average results for each batch are not in accordance with the specification. All tests should be made on the Contractor’s expense.

All steel is to be totally free from dirt, paint, loose rust or scale when in position ready for concreting.

The Contractor shall cut and bend bars to BS 4466 and to schedule provided unless otherwise instructed by the Project Manager.

Straight sections of bars must be kept out of winding. The internal radius of bends shall in no case be less than four times the diameter of the bar, except for stirrups, column binders, and wall shear bars which are to be bent to fit closely around the main bars.

Great care is to be taken to bend stirrups and columns binders separately and to the sizes shown.

All bars will be cut and bent cold using approved machines.

Lengthening of bars by welding, and rebending of incorrectly bent bars will not be permitted, except where requested by the Project Manager.

The Contractor shall provide on site facilities for hand bending to deal with minor adjustments.

Unless otherwise allowed for in the particular specification splices in reinforcing bars shall be formed by lapping. Such laps in bars in any member shall be staggered. Except as otherwise indicated on the drawings the minimum overlap of lapped splices shall be 50 bar diameters or 400mm whichever is greater.

The steel is to be fixed in position exactly as indicated, and the bars are to be securely wired together with 1.6 or 1.4mm soft galvanized iron wire or approved spring galvanized steel clips wherever necessary to prevent any displacement during concreting.

Spacers, chairs and the like, temporary or permanent, are to be used as required to ensure that the steel has the exact amount of cover indicated. No permanent spacers may show on a surface where a fair faced concrete finish or a brushed aggregate finish are required. Type of spacers shall be approved by the Project Manager before starting the work.

Unless otherwise indicated, the minimum cover to the reinforcing bars is to be as listed below or equal to the diameter of the bar, whichever is greater.

Position Minimum cover - 				mm

Main bars in internal faces of columns and beams 		25

Main bars in external faces of columns and beams 		25

Main bars in floor slabs and soffits of roof slabs 		20

Main bars in top of roof slabs 				20

Outermost bars in internal faces of walls 			25

Outermost bars in external faces of walls 			25

Bars in top of ground slabs 					30

Bars near faces in contact with soil 				50

The placing of all reinforcement will be checked by the Project Manager and in no case is concrete to be poured around any steel that has not been passed by him. The Contractor is to ensure that no steel is displaced from its position during the placement of concrete and until the concrete is set.

The insertion of bars into or removal of bars from concrete already placed will not be permitted.

Reinforcement temporarily left projecting from the concrete at the joints shall not be bent without the prior approval of the Project Manager.

Secondary reinforced concrete members for which no reinforcement details are given in the drawings or the

Bill of Quantity shall have a minimum ratio of reinforcement area to concrete area of 0.33 %.

    - Concreting

      - Cement

The cement used shall be Portland Cement conforming in all respects to BS EN 197-1:2000, unless otherwise required, bags shall contain 50kg net + 1%.

The Contractor shall at all times furnish the Manufacturer's statement of the above Standard Specifications together with the date of manufacture, certified by an independent agency in the country of origin approved by the Project Manager.

The cement shall be delivered to the site by the Contractor in the original sealed and branded bags or containers of the manufacturer in batches not exceeding 100 tons and shall be stored in a proper manner off the ground to prevent deterioration. Each batch shall be stacked separately and used in the order of delivery.

No cement shall be used which has been manufactured more than twelve months prior to its proposed use on site.

All cements whether stored in bulk, bags, or containers in warehouses or on site shall be sampled for testing according to ASTM C183 (Methods of Sampling Hydraulic Cements). Test samples over and above those specified shall be taken at any time if so requested by the Project Manager. Testing of cement shall be in accordance with the methods required by BS EN 197-1:2000 or any other accepted by the Project Manager.

      - Aggregates

This specification covers fine and coarse aggregates other than lightweight aggregates for use in the production of concrete.

When lightweight aggregates are required they will be defined in the BOQ.

The aggregates shall be crushed gravel or stone and shall comply with BS 882 for graded or single size aggregate and shall be obtained from any quarry in the mountains approved by the Project Manager.

For convenience part of Clause 5 of BS 882 (grading) including Tables 1, 2 and 3 are reproduced herein.

Coarse aggregate: the grading of coarse aggregate, when analysed by the method given for sieve analysis in

BS EN 1097 shall be within the limits given in Table 1.

Fine aggregate: the grading of a fine aggregate, when analysed by the method of sieve analysis described in

BS EN 1097, shall be within the limits of one of the grading zones given in Table 2, except that a total tolerance of up to 5 per cent may be applied to the percentages under-lined. This tolerance may be split up; for example, it could be 1 per cent on each of three sieves and 2 per cent on another, or 4 per cent on one sieve and 1 per cent on another.

The fine aggregate shall be described as fine aggregate of the grading zone into which it falls, e.g. BS 882, Grading Zone 1.

NOTE: It is intended that individual zones should not be specified in contract documents relating to concrete but that the concrete mixes should be modified to make the best use of the materials readily available.

If approved by the Project Manager. Single-sized aggregate to BS 882 Table 1 may only be used for reinforced concrete when combined in two or more sizes to provide a well-graded mixture approved by the Project Manager.

Sampling and testing of aggregates shall be as required by BS 882 and in accordance with BS 812 'Methods for Sampling and Testing of Mineral Aggregates, Sands and Fillers'. All sampling shall be done by or under the supervision of the Project Manager.

The combined percentage of sulphates and chlorides by weight in coarse and fine aggregates shall not exceed 0.05 per cent (500ppm) of the combined weight of total aggregates.

Just before use the aggregate will be washed down with potable water to reduce the content of sulphates, chlorides and other extraneous material.

The choice and preparation of sites for stockpiling of aggregates, the number and sizes of stockpiles and the methods adopted to prevent segregation of component sizes shall be agreed with the Project Manager.

Coarse aggregate shall be stockpiled in three separate gradings: 38-19mm, 19-10mm, 10-5mm. When aggregates of different gradings are stockpiled close together the stockpiles shall be separated by bulkheads.

Stockpiles are to be on concrete or other hard surface sufficiently sloped so that water is not retained in the base of the stockpiles .

All aggregates are to be handled from the stockpile in such a manner as to secure a typical grading of the material, care being taken to avoid crushing the aggregates and contamination with extraneous matter.

Aggregates need not be stockpiled when a crushing-screening plant is used in tandem with a batching plant properly equipped with several bins for different sized aggregates having the appropriate weighing scales at such bin such that a mix of the desired gradation is obtained consistently and the whole operation is conducted to the satisfaction of the Project Manager.

      - Water

Unless otherwise authorised in writing by the Project Manager, only chilled water from potable supply system may be used for mixing concrete and other products containing cement.

Similarly only potable water may be used for curing concrete and cement products during the first 24 hours after pouring. Later, fresh water, or other water containing not more than 4750 ppm dissolved solids of which not more than 1000 ppm may be chlorides, may be used for curing.

No additives of any kind shall be used in the concrete without the express approval in writing of the

Project Manager.

      - Quality Of Concrete

Concrete shall be a mixture of cement, aggregates and water as covered respectively by 5.1.4.1 to  5.1.4.3 above.

The mix proportions, workability and strengths of the various types of concrete shall conform to Table 4.

The terms contained in Table 4 are defined as follows: WATER/CEMENT RATIO: the term water/cement ratio means the ratio by weight of the water to the cement in the mix, expressed as a decimal fraction. The water is that which is free to combine with the cement in the mix.

This includes free water in the aggregate but excludes water absorbed or to be absorbed by the aggregate.

The aggregate for this purpose shall be taken in a saturated surface-dry condition.

The absorption of the aggregates shall be determined in accordance with BS EN 1097 or any other method approved by the Project Manager.

The strengths specified are for ordinary Portland cement to BS EN 197-1:2000; if other types of cement are specified, the required strength shall be as defined in the Bills of Quantities.

The cubes used for the compression tests shall be 150x150x150 mm as specified in BS 1881. In case cylinders are used for determination of concrete compressive strength in accordance with ASTM C 39, the corresponding cube strength shall be obtained by using a multiplication factor of 1.2.

AGGREGATE/CEMENT RATIO: the term aggregate/cement ratio means the ratio by weight of aggregate to cement in the mix. For this purpose the aggregate is taken in a saturated surface-dry condition as for the water/cement ratio above.

FINE/TOTAL AGGREGATE RATIO: the term fine/total aggregate ratio means the ratio by weight of the fine aggregate to the total aggregate in the mix expressed as a percentage. For this purpose the aggregate is also taken in a saturated surface-dry condition as for the water/cement ratio above.

VOLUME OF AIR ENTRAINED: the air content expressed as a percentage by volume of concrete shall be determined by ASTM C231, 'Air Content of Freshly Mixed Concrete by the Pressure Method '. At least one test for each 120 cubic meters of concrete shall be made.

SLUMP: the slump of the freshly mixed concrete shall be determined in accordance with BS EN 12350-

2:2000. At least one morning and one afternoon test shall be made and whenever directed by the

Project Manager.

STRENGTH OF CONCRETE: Preliminary Test Cubes shall be taken from the trial mixes designed to select the job mix and shall be made and tested in accordance with BS EN 12390-3:2002.

SAMPLING FOR COMPLIANCE TESTING: Works Test Cubes shall be those used for control during construction and shall be made and tested in accordance with BS EN 12350-1:2000 and BS EN 12390-2:2000.

The Contractor when tendering having knowledge of the source and types of cement, aggregate, plant and method of placing he intends to use shall allow for the aggregate/cement ratio and water/cement ratio which he considers will achieve the strength requirements specified and will produce a workability which will enable the concrete to be properly compacted to its full depth and finished to the dimensions and within the tolerances shown on the Drawings. In any event the aggregate/cement ratio and the water/cement ratio shall not exceed the upper limits specified in Table 4 for each type of concrete. Furthermore, the quantity of cement per cubic metre of concrete shall in no case be less than the minimum specified in Table 4.

As soon as possible after signature of the Contract, the Contractor shall prepare such trial mixes as required to satisfy the Project Manager that the specified concrete strengths will be obtained using the materials and mix proportions in accordance with the above clauses. The proportion of cement shall be increased if necessary to obtain the strengths required.

From each trial mix, six Preliminary Test Cubes shall be made and tested at 7 days and four at 28 days, the test at 7 days being intended to give and early indication of possible variation from the required strength. If the difference between the highest and lowest test results from any one trial mix is more than 15 per cent of the average of the strength test results, the test is to be discarded and a further trial mix made, unless all test results so obtained are above the required strength. Separate trial mixes are required for each type of concrete. The trial mix or mixes agreed by the Project Manager shall be designated job mixes and used as a basis for actual concrete production.

      - Batching And Mixing Of Concrete

All concrete shall be batched by weight and mixed mechanically. Hand mixing shall not be allowed except only upon the written permission of the Project Manager.

Concrete may either be batched and mixed on site or outside the site and transported thereto.

When mixed outside the site and transported to it, batching and mixing shall be in accordance with ASTM Specification C94. 'Standard Specification for Ready-Mixed Concrete'.

When mixed on site, batching and mixing shall be as follows:

BATCHING BY WEIGHT: The cement and each size of aggregate shall be measured by weight. The water may be measured by weight or volume. The weight-batching machines used shall be of a type approved by the Project Manager and shall be kept in good condition while in use on the Works. Checks are to be made as required by the Project Manager to determine that the weighing devices are registering correctly.

BATCHING AGGREGATE BY VOLUME: When batching aggregates by volume is allowed as and when required, the cement shall be batched by weight and the water by weight or volume. Each size of aggregate shall be measured in metallic containers the depth of which is at least equal to their greatest width. The containers shall be of such shape that their volume can be easily checked by measurement.

MIXING CONCRETE: the location of the batching and mixing plant shall be agreed with the Project Manager.

The amount of concrete mixed in any one batch is not to exceed the rated capacity of the mixer. The whole of the batch is to be removed before materials for a fresh batch enter the drum.

On cessation of work, including all stoppages exceeding 20 minutes, the mixers and all handling plant shall be washed with clean mixing water. If old concrete deposits remain in the mixer drum, they shall be rotated with clean aggregate and water prior to production of new concrete.

Concrete mixed as above is not to be modified by the addition of water or in any other manner to facilitate handling or for any other reason.

      - Work In Cold Or Hot Weather

Concrete is not to be mixed or placed at a shade air temperature bleow 2 deg .C on a rising thermometer or at a shade air temperature bleow 3 deg .C on a falling thermometer.

When the shade air temperature is 25 deg .C and rising, special precautions shall be taken during concerting operations, such as shading of the aggregates and plant, cooling of the mixing water or other methods approved by the Project Manager, so that the temperatures of the concrete when placed shall not be in excess of 32 deg .C.

Fresh concrete placed at these temperatures shall be shaded from the direct rays of the sun to the satisfaction of the Project Manager for a period of at least 24 hours.

      - Placing

Concrete shall be conveyed from the mixer to its final position in any suitable manner , provided there is no segregation , loss of ingredients or contamination.

It shall be placed in its final position before initial setting takes place and within 20 minutes of the addition of the water to the mixer without using any additives. In case additives will be used, the manufacturer specifications of such additives must be handed over to the Project Manager to be approved before using it.

The order of placing concrete shall be such as to prevent water from collecting at the ends, corners and along the faces of froms. It shall not be placed in large quantities at a given point and allowed to run or be worked over a long distance in the form.

Whenever possible concrete shall be placed and compacted in even layers with each batch adjoining the previous one.

The thickness of the layers shall be between 150 and 300mm for reinforced concrete and up to 450mm for plain (non-reinforced) concrete, the thickness depending on the width of forms, the amount of reinforcement and the need to place each layer before the previous one stiffens.

Concrete shall not be allowed to drop freely for more than 2 metres. To convey the concrete as near as possible to its final position, drop chutes of rubber or metal shall be used for small sections and bottom dump buckets or other suitable vessels for large sections.

Concrete shall be carefully compacted when placed to ensure a dense and uniform mass free from air holes and cavities. Concrete type "A" and "B"shall be compacted by vibration. Vibration shall be performed by mechanical or electro -mechanical vibrators. The vibrators shall be of the plunger (poker) type for insertion in the concrete: except that plate type vibrators ( external ) shall be used if requested by the Project Manager.

The plunger (poker) type vibators shall have a diameter compatible with the lowest spacing of reinforcement, a sufficiently high frequency and be properly handled by experienced personnel. They hall be immersed at regular intervals close enough to vibrate all of the concrete , but not too close to affect previously vibrated and partially set concrete . Each immersion shall continue until shortly after air bubbles cease to appear on the surface of the concrete, but shall not last more than 30 seconds. The vibrators shall be withdrawn gradually and vertically to ensure that no air pockets are formed.

When external vibrators are used as directed by the Project Manager, they shall be clamped to the forms whenever possible to avoid large impact during handling, and the forms shall be so constructed as to withstand the additional vibrations.

All vibrations, compaction and finishing operations shall be completed within 15 minutes from the time of placing the concrete in its final position. Until it has hardened sufficiently to carry weight without distortion, workers shall not be allowed to walk over freshly placed concrete.

Concreting of any one part or section of the work shall be carried out in one continuous operation, and no interruption of concreting work will be allowed without the approval of the Project Manager. Where beams and slabs together form an integral part of the structure they shall be poured in one operation.

A record is to be kept by the Contractor on site of the time and date of placing the concrete in each portion of the works and the number and identification of the Works Test Cubes, corresponding to these portions. Such records are to be handed to the Project Manager weekly during the progress of the work .

      - Admixtures

No admixtures of any type shall be used in the preparation of concrete or concrete products unless so required or directed by the Project Manager. In case any such admixtures are used the rates and methods of application shall be strictly in accordance with the manufacturer's instructions which must be approved by the Project Manager before using it.

      - Joints

- Working joints in the concrete will be permitted only in places marked on the Drawings or as approved by the Engineer.

- Working joints will not be measured for payment and Contractor will incorporate their cost in the unit prices for concrete works.

- Joints with P.V.C water stops will be constructed as marked on the Drawings or requested by the Engineer.

- The water stops will be of P.V.C strips 240 x 4 mm. supplied by an approved manufacturer and approved by the Engineer. Contractor must furnish samples of water stop to be used along with the manufacturer’s certificate specifying the characteristics and quality of the material.

- Engineer’s approval of the sample does not release the Contractor from any responsibility to the quality of the material and the proper execution of the joint.

- Water stops will be furnished to the site as complete units having the shape and dimensions as indicated on the Drawings.

- The edges of the water stop will be joined by welding since no overlap will be permitted.

- The water stop will be inserted accurately in the elements of the structure cast first and will be properly protected from any damage, dirt or distortion of its shape and position. Prior to casting the adjoining part of the concrete element, face of the joint will be properly cleaned and a 3 mm. hot asphalt coat will be applied on the whole of the joint area. Sealing of joints shall be completed by filling the groove with an elastoseal pack as marked on the Drawings.

      - Curing

- Materials

Hessian or Burlap : They shall be clean and free from harmful materials. Their unit weight shall be not less than 230g/.m3

Impermeable membranes : The following impermeable membranes may, with the Engineer’s approval, be used.

Clear polyethylene film with no holes, tears, scratches and contamination of any type.

Hessian coated with white polyethylene of density not less than 300g/sq.m. The coating may be on one side only but shall be not less than 0.1mm thick and shall not peel during and after use.

Curing Compounds : These shall conform to AASHTO M148 (ASTM-C309).

Sand : It shall be natural sand free of silt and clay and contaminants which can be harmful to the concrete.

Water : It shall satisfy the requirements of Section 3.2  of the Specification.

- Method of Curing

General : The method of curing to be used shall be approved by the Engineer. It shall not cause any undesirable blemishes such as surface discoloration and surface roughness. Curing compounds shall not be used  on construction joints and surfaces that are to receive waterproofing, paint or membranes.

Ponding : Curing by ponding may be used for horizontal surfaces such as bases, pile caps and slabs. Large areas of horizontal surfaces shall be separated into ponds not exceeding 5 sq.m. The ponds shall first be filled between 12 to 24 hours after pour, unless otherwise authorized by the Engineer, and shall be replenished from time to time so as to maintain the ponding for the specified curing period. The concrete temperature and the temperature of the curing water shall be not greater than 20C.

Sprinkling : Unless otherwise approved by Engineer, curing by spraying shall commence between 12 to 24 hours after the concrete pour. The concrete shall be maintained damp at all times during the curing period by periodic light sprays.

Wet Hessian / Burlap : Members to be cured by wet Hessian or wet Burlap shall be completely wrapped with the material which shall be kept moist at all times during the curing period by regular spraying. Unless otherwise approved by the Engineer, the overlap under normal conditions shall be not less than one-quarter the width of the Hessian or Burlap and not less than one-half the width in windy and/or rainy conditions. Before members are wrapped for curing, they shall first be evenly moistened. Unless approved by the Engineer,  Burlaps shall be supplied only in rolls and Burlap bags shall not be used. Second-hand  Hessian and Burlap, if approved for use, shall be clean without holes and contamination of any kind that can affect the concrete.

Waterproof Sheets : Waterproof sheets used for curing shall, unless directed by the Engineer, be spread immediately after the pour. The sheet shall, unless approved by the Engineer, be clear of the concrete surface but be arranged in such a manner as to prevent the movement air over the concrete surface. Waterproof sheets shall not be used when the air temperature is 25oC or higher.

Curing Compounds : Curing compounds shall be applied in two applications at a coverage rate of not less than 1 Ltr/ 7.4 sq.m. per application or as recommended by manufacturer.

The first coat shall be applied immediately after the removal of the forms and the acceptance of the concrete finish and after the disappearance of free water on unformed surfaces. If the concrete is dry or becomes dry, it shall be thoroughly wetted with water and curing compound applied just as the surface film of water disappears. The second application shall be applied after the first application has set. During curing operations, any unsprayed surfaces shall be kept wet with water. The curing membrane will not be allowed on areas against which further concrete is to be placed.

Hand operated spray equipment shall be capable of supplying a constant and uniform pressure to provide uniform and adequate distribution of the curing membrane at the rates required. The curing compound shall be thoroughly mixed at all times during usage.

The curing membrane shall be protected against damage for the entire specified curing period. Any coating damaged or otherwise disturbed shall be given an additional coating. Should the curing membrane be continuously subjected to injury, the Engineer may require wet burlap, polyethylene sheeting, or other approved material to be applied at once.

No traffic of any kind will be permitted on the curing membrane until the curing period is completed, unless the Engineer permits the placement of concrete in adjacent sections, in which case the damaged areas shall be immediately repaired as directed.

Steam Curing

Low Pressure Steam Curing : This shall be in accordance with recommendations of ACI 517.

High Pressure Steam Curing : This shall be in accordance with the recommendations of ACI 516.

iii) Curing Time

A	The minimum curing time shall be the number of days given in the Table below unless the average surface temperature of the concrete during the required number of days falls below 10C, in which case the period of curing shall be extended until the maturity of the concrete reaches the value given in the following Table:

NORMAL CURING PERIODS

| Minimum periods of protection for different types of cement |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Conditions under which concrete is maturing | Number of days (where the average surface temperature of the concrete exceeds 10؛C during the whole period) |  |  | Equivalent maturity (degree hours) calculated as the age of the concrete in hours multiplied by the number of degrees Celsius by which the average surface temperature of the concrete exceeds minus 10؛C. |  |  |
|  | Other* | SRPC | OPC or RHPC | Other* | SRPC | OPC or PHPC |
| 1.Hot weather or drying winds | 7 | 4 | 3 | 3500 | 2000 | 1500 |
| 2. Conditions not covered by 1. | 4 | 3 | 2 | 2000 | 1500 | 1000 |

NOTE Other* includes all permitted cements except OPC, PHPC and SRPC.

KEY. 	OPC   = Ordinary Port land Cement

RHPC = Rapid-hardening Portland Cement.

SRPC  = Sulfate Resisting Portland Cement.

B	The minimum curing time given in the Table above shall be compared with the time required for cubes, cured under identical conditions to those which the concrete is subjected to, attain 70% of the characteristic strength. The greater shall be taken as the minimum curing time.

      - Formed Finishes

1 - Basic finish

General requirements:

(a) Produce an even finish with a sheet material.

(b) Arrange panels in a regular pattern.

(c) Blowholes not more than about 10mm in diameter will be permitted but otherwise surface is to be free from voids honey combing and other large defects.

(d) Variation in colour resulting from the use of an from discolaration due to contamination or grout leakage.

The finish will be left as struck; making good or small defects will normally be permitted but only after inspection by the Project Manager. All blowholes shall be filled with a matching mortar to an approved sample unless otherwise instructed by the Project Manager. All faces shall be protected from damage, especially arrisses.

All faces shall be protected from rust marks and other surface disfigurements. Form tie holes shall be filled with a matching mortar to an approved sample accepted by the Project Manager .

2 - Fine finish ( Fair Face)

General Requirements:

a) Produce a smooth even finish with an impervious sheet metal.

b) Make panels as large as is practicable and arrange to approval.

c) Blowhole not more than about 5mm in diameter will be permitted but otherwise surface is to be free from voids, honey combing and other defects.

d) Variation in colour resulting from the use of an impervious form lining will be permitted, but the surface is to be free from discoloration due to contamination or grout leakage.

e) Concrete cover spacers shall be used only if approved.

The finish is to be left as struck. Making good will not normally be permitted. All form tie holes are to be filled with a matching mortar to an approved sample. Wire form ties shall not be used. Approval of the

Project Manager for the position of tie holes is to be obtained before use.

      - Quality Control Testing Etc.

Prior to commencing the work the contractor shall make available on site the following minimum approved equipment kept in good condition at all times :

- Six Cube moulds.

- Slump cones.

- Thermometer.

- Any other accessories as required by the Project Manager.

All samples and testing shall be done in the presence of the Project Manager or his authorized representative either on site or in an approved testing laboratory in the area.

The frequency of testing shall be as noted in the clauses of this section and whenever required by the

Project Manager.

The works Test Cubes shall be made as follows for types of concrete (A) and (B):

(a) At least three times weekly per mixing plant.

(b) At least once for three individual parts of the structure.

(c) At least once per 100 cubic meters of Concrete or fraction thereof.

At least six cubes shall be made at one time. Two of the six cubes are to be tested at seven (7) days. The remaining four cubes are to be tested at 28 days, and their average strength must not fall below the minimum strength specified for each type of concrete and the lowest test result shall not be more than 20% below the average of the four cubes.

When the result of 7-day test is unsatisfactory, the Contractor may elect to remove and replace the defective concrete without waiting for the 28-day test. If the result of the 28-day test is unsatisfactory all concreting shall be stopped at the Contractors expense and shall not proceed further without the written permission of the Project Manager.

The Contractor shall then, in accordance with the instructions of the Project Manager, remove cores and test same or conduct in- situ tests in accordance with CP 144 from or on suspect portions of the works, under the supervision of the Project Manager.

Concrete judged by the Project Manager to be defective shall be forthwith cut out, removed and replaced at the Contractors own expense.

In the event of strengths consistently higher than those specified being obtained, a reduction in the number of tests may be authorized by the Project Manager.

      - Position of Reinforcement

The actual concrete cover to all steel at any point should not be smaller than the required nominal cover by more than 5mm.

The effective depth of fully or nearly fully stressed tensile reinforcement should not be less than that given on the drawings by an amount exceeding 5 per cent of the effective depth of the section being considered or

5mm whichever is the greater.

      - Ready mixed concrete

Ready - mixed concrete as defined in BS 1926 , batched off the site will be used with agreement of the Project Manager and shall comply with all requirements of the Contract . The quality and strength of cements shall be determined by site tests. No test results supplied by Ready-Mix Supplier shall be accepted as proof of the quality and strength of the concrete.

The concrete shall be carried in purpose made agitators operating continuously, or in truck mixers. The concrete shall be compacted and in its final position within 1 hour of the introduction of cement to the aggregate or as agreed by the Project Manager. The time of such introduction shall be recorded on the Delivery Note together with the weight of the constituents of each mix.

When truck mixed concrete is used, water shall be added under supervision either at the site or at the central batching plant as agreed by the Project Manager but in no circumstances shall water be added in transit.

Unless otherwise agreed by the Project Manager Truck mixer units and their mixing and discharge performance shall comply with the requirements of BS 4251. Mixing shall continue for the number and at the rate of revolutions recommended in accordance with BS 4251 or, in the absence of the manufacturer's instructions, mixing shall continue for not less than 100 revolutions at a rate of not less than 7 revolutions per minute.

Prior to any ready mixed concrete being ordered, the Contractor shall submit to the Project Manager details of the supplier and shall arrange for the Project Manager to inspect the supplier's works if required.

Truck-mixer units shall be maintained and operated strictly in accordance with the manufacturer's recommendations.

      - Concrete Surface Hardener

Monolithic surface hardening compound to provide a highly abrasion resistance surface with a dry shake method.

The abrasion resistance of the hardening compound shall comply to BS 784 1953, and the compressive strength not less that 70N/mm2 after 28 days, tested according to the BS EN 12390.

The hardening compound shall be applied in rate of 7 kg/m2 on the floor surface at the time when the concrete has stiffened to the point when light foot tradfic leaves an imprint of about 3mm.

The hardening compound shall be applied in two application stages:

Stage 1: using ½ to ⅔ of the required material. When the material becomes uniformly dark by the absorption of moisture from concrete then the floating can be applied.

Stage 2: spreading the remaining material on the surface, and apply floating to the surface after the moisture being absorbed.

Final finishing of the floor shall be done using mechanical trowelling machine when the floor has stiffened sufficiently.

Curing for the surface shall be applied as clarified above.

    - Construction of Manholes

      - General

- The Contractor shall construct manholes in reinforced cast-in-place concrete or in precast concrete rings to the levels, dimensions and shapes shown on the Drawings, or as directed by the Engineer.

- All manholes shall be constructed with incoming and outgoing pipes neatly and truly concreted in, complete with cast iron steps and manhole cover and frame as here specified and shown on the Typical Drawings.

      - Manholes

- The Contractor shall construct a well compacted blinding layer of plain concrete Type B 150 to the required levels after the Engineer has inspected and approved bottoms of excavations. The surface of the blinding layer shall be regular and smooth.

- The Contractor shall set tops of manhole frames and covers to the elevations as indicated on Drawings, unless otherwise directed.

- All items built into walls of manholes and structures such as pipe ends shall be adequately sealed to obtain watertight construction to the satisfaction of the Engineer. Steps shall be installed in a staggered pattern to the extent indicated at not more than 300 mm centers and shall be well grouted.

- Drilling shall be used when connecting pipes into manholes.

- Covers and frames shall be well centered and anchored all around to the approval of the Engineer.

- After the installation of the cast iron frames, the Contractor shall provide plain concrete Type B 200 in surrounds as indicated on Drawings. Surrounds shall be well hunched all round and trowelled smooth.

- All manholes steps, covers and it’s frames shall be well cleaned and painted with black paint of bituminous base after complete installation and to the approval of the Engineer.

      - Cleaning

- All manholes shall be cleaned of any accumulation of silt, mortar, debris or other foreign matter and shall be free of any such accumulation at the time of final inspection.

      - Reinstatement of Staircases

- Staircases shall be reinstated as shown on the Typical Drawings and the type of reinstatement shall be decided by the Engineer according to the equal to that before the work began.

      - Black Bitumen Paint

The black bitumen paint shall be applied in the thickness and number of coats described in the BOQ or drawings, and to be applied with a coverage rate of 8m2/litre for concrete surfaces.

All surfaces must be sound and free from dust, dirt, all loose material, grease and oil etc., and dry before applying the black bitumen paint.

The black bitumen paint shall comply to BS 3416 Type I nad II, as well as BS 476: Part 7 class 1 fo fire resistance.

# Special Specifications

# GEOMEMBRANE LINER

PART 1 - GENERAL

1.01	DESCRIPTION:

Furnish all labor, materials, tools and equipment and perform all operations necessary for installation and testing of the geomembrane, as described herein, in associated specifications, and shown on the Drawings.

Provide quality assurance as described in this specification for the manufacture, supply, and installation of textured and smooth geomembrane as specified.

The geomembrane material shall be High Density Polyethylene (HDPE).

A 2 mm Textured High Density Polyethylene (THDPE) geomembrane shall be utilized on the side slopes of the  polishing ponds beds   The THDPE shall be textured on both sides.

A 2 mm smooth finish High Density Polyethylene (HDPE) geomembrane shall be utilized under the polishing ponds  beds as indicated on the BOQ and drawings.

1.02	RELATED WORK:

- General Requirements

- Earth Excavation, Backfill, Fill and Grading

Concrete works

  - REFERENCES:

- ASTM Standards

  - D 638:  	Test Method for Tensile Properties of Plastics

  - D 792:		Specific Gravity (Relative Density) and Density of Plastics by Displacement.

  - D 1004:	Test Method for Initial Tear Resistance of Plastics Film & Sheeting.

  - D 1238:	Test Method for Flow Rates of Thermoplastics by Extrusion Plastometer.

  - D 1505:	Test Method for Density of Plastics by the Density-Gradient Technique.

  - D 1603:	Test Method for Carbon Black in Olefin Plastics.

  - D 3895:	Test Method for Oxidative Induction Time of Polyolefins by Thermal

Analysis.

  - D 4218:	Test Method for Determination of Carbon Black Content in

Polyethylene Compounds by the Muffle-Furnace Technique.

  - D 4833:	Test Method for Index Puncture Resistance of Geotextiles,

Geomembranes and Related Products.

  - D 1557:	Test Method for Laboratory Compaction Characteristics of Soil

Using Modified Effort (2,700 KN-M/M3).

  - D 4437:	Standard Practice for Determining the Integrity of Field Seams

Used in Joining Flexible Polymeric Sheet Geomembranes.

  - D 5199:	Test Method for Measuring Nominal Thickness of Geotextiles and

Geomembranes.

  - D 5321:	Test Method for Determining the Coefficient of Soil & Geosynthetic

Or Geosynthetic and Geosynthetic Friction by the Direct Shear Method.

  - D 5397:	Procedure to Perform a Single Point Notched Constant Tensile

Load – Appendix (SP-NCTL) Test.

  - D 5596:	Test Method for Microscopic Evaluation of the Dispersion of Carbon

Black in Polyolefin Geosynthetics.

  - D 5721:	Practice for Air-Oven Aging of Polyolefin Geomembranes.

  - D 5885:	Test Method for Oxidative Induction Time of Polyolefin Geosynthetics

By High Pressure Differential Scanning Calorimetry.

  - D 5994:	Test Method for Measuring the Core Thickness of Textured

Geomembranes.

GRI Standards:

  - GM 10:	Specification for the Stress Crack Resistance of Geomembrane Sheet.

  - GM 11:	Accelerated Weathering of Geomembranes using a Fluorescent

UVA-Condensation Exposure Device.

  - GM 12:	Measurement of the Asperity Height of Textured Geomembranes

Using a Depth Gage.

U.S. Environmental Protection Agency Technical Guidance Document “Quality Control Assurance and Quality Control for Waste Containment Facilities,” EPA/600/R-93/182, September 1993, 305 pages.

1.04	QUALITY ASSURANCE:

- Manufacturing:

  - The Manufacturer of the selected geomembrane shall have successfully manufactured a minimum of 1,000,000 m2 of the selected geomembrane material and shall be listed by the National Sanitation Foundation (NSF) Standard 54 as meeting all the requirements for flexible geomembranes.

- Installation:

  - The Installation Contractor shall be the manufacturer, or an agent licensed by the manufacturer and specially trained to install the manufacturer's material.

  - The Contractor shall employ a single installation supervisor for the duration of the work who shall have the responsibility of directing all geomembrane layout, seaming, patching, testing, repairs, and all other activities by the Installer.  The Installer's supervisor shall have installed or supervised the installation and seaming of a minimum of 100,000 m2 of the selected geomembrane material using the same type of seaming apparatus specified for this project.

1.05	SUBMITTALS:

- Submit the following in accordance with Section 01300 - two weeks prior to Geomembrane Installation:

  - Contractor to furnish for approval four weeks prior to installation a Panel Layout Plan identifying all seams and details.

  - Certification from the manufacturers resin supplier that all resin used in the manufacturing of the material for this job meets the specification.

  - Copies of quality control certificates issued by the resin supplier.

  - Certification that the geomembrane and extrudate to be used at this project have the same properties and are the same material.

  - Certified quality control certificates to show conformance with Parts 2.02 and 2.03 of this specification.

  - Written instructions from the manufacturer for the storage, handling, installation, seaming, and repair of the geomembrane material.

  - Certification from the Contractor's on site representative that the surface on which the geomembrane is to be installed is acceptable for such installation.

  - Certification that the minimum friction angle/adhesion values at the interface of the THDPE geomembrane with the overlying material and underlying soils meet requirements as determined by ASTM D 5321.  Requirements and testing procedures are specified in Part 2.04.

- Submittals Upon Completion of Installation:

  - Written documentation from Contractor's Installation Supervisor for each day's work.  As a minimum, the documentation should contain the following:

    - Subgrade acceptable for geomembrane placement (i.e., no rocks, roots, or other protrusions that could damage the cap).

    - Temperature and weather conditions, and statement that conditions were suitable, during field seaming.

    - Field seams:

      - Seams clean and dry.

      - Minimum overlap for seaming method utilized met.

      - Wrinkles in seam repaired.

      - Field seams inspected and tested in accordance with this specification.

    - Geomembrane:

      - Free of punctures, tears, scuffing.

      - Location of repairs shown on the Panel Layout Plan.

      - Location of pipe penetrations and boots installed properly.

    - Results of all daily field tests as required in this specification.

  - Written certification as to occurrence of Final Walk Over (Part 3.04) and any remedial action taken as a result of defects discovered.

  - At completion of laying down of materials above geomembrane, the Contractor shall issue written certification that laying down of materials  operations have proceeded as directed and are acceptable.

1.06	WARRANTIES:

- Prior to completion of installation, the Contractor shall issue a written warranty from the geomembrane supplier to the Owner for the quality of the material for a period of 20 years.

- Prior to completion of installation, the Contractor shall issue a written warranty to the Owner for the workmanship of the installation for a period of 20 years.

PART 2 - PRODUCTS

2.01	ACCEPTABLE MANUFACTURERS:

- GSE Lining Technologies Inc.,

19103 Gundle Road

Houston, TX  77073-3515 USA

(281) 230-8695

Attn: Mark Harris

Poly-Flex Inc.

2000 W. Marshall Dr.

Grande Praire, TX  75051-2709 USA

(972) 337-7314

Attn: George Yacdani

Serrot International Inc.

125 Cassai Way

Henderson, NV 89014 USA

(702) 566-8600

Attn: Fred Staab

Approved equal.

2.02	MATERIAL:

- The material shall consist of a single ply THDPE or HDPE geomembrane of a minimum 6 m seamless width with no additives, fillers, or extenders.  The material shall be manufactured of new, first quality resin compounded and manufactured specifically for the intended purpose.

The selected geomembrane shall have the following minimum physical properties as determined by the appropriate test method and testing frequency:

| Property | Test Method | Test Value HDPE | Test Value THDPE | Testing Frequency (minimum) |
| --- | --- | --- | --- | --- |
| Thickness (min. ave) (1), (2) | ASTM D 5199 | 2 mm | -- | per roll |
|  | ASTM D 5994 | -- | 2 mm (-5%) |  |
| Asperity Height (mils) | GRI GM 12 | -- | 0.25 mm | every 2nd roll |
| Density (min. ave.) | ASTM D 1505 | 0.94 g/cc | 0.94 g/cc | 90,000 kg |
| Carbon Black Content (range) | ASTM D 1603 | 2-3% | 2-3 | 9,000 kg |
| Carbon Black Dispersion | ASTM D 5596 | 10 different views all in Categories 1 or 2 |  | 20,000KG |
| Tensile Properties (min. ave.)(3) - Yield Strength - Break Strength - Yield Elongation - Break Elongation | ASTM D 638 (Type IV ) | 22 kN/m 40 kN/m 12% 700% | 22 kN/m 16 kN/m 12% 100% | 9,000 kg |
| Tear Resistance (min. ave.) | ASTM D 1004 | 187 N | 187 N | 20,000 kg |
| Puncture Resistance (min. ave.) | ASTM D 4833 | 480 N | 400 N | 20,000 kg |
| Stress Crack Resistance (4) | ASTM D 5397 (app) | 200 hr. | 200 hr. | Per GRI-GM10 |
| Oxidative Induction Time (OIT) (min. ave.) (5) (a) Standard OIT -or- - High Pressure OIT | ASTM D 3895 ASTM 5885 | 100 min. 400 min. | 100 min. 400 min. | 90,000 kg |
| Oven Aging at 85oC (5),(6) - Standard OIT (min. ave) % retained after 90 days -or- - High Pressure OIT (min. ave.) % retained after 90 days | ASTM D 5721 ASTM D 3895 ASTM D 5885 | 55% 80% | 55% 80% | per each formulation |
| UV Resistance (7) High Pressure OIT (min. ave.) % retained after 1600 hr. (8) | GRI GM 11 ASTM D 5885 | 50% | 50% | per each formulation |

- For HDPE geomembrane, the lowest individual thickness measurement out of 10 values shall have a variation no greater than minus 10 percent.

- For THDPD geomembrane, the lowest individual thickness measurement for 8 out of 10 values shall have a variation no greater than minus 10 percent.  The lowest individual thickness measurement out of 10 values shall have a variation no greater than minus 15 percent.

- Machine direction (MD) and cross machine direction (XMD) average values should be on the basis of 5 test specimens each direction.  Yield elongation geomembrane calculated using a gage length of 33 mm.  Break elongation calculated using a gage length of 50 mm.

- The yield stress used to calculate the applied load for the SP-NCTL test should be the manufacturer’s mean value via MQC testing.  The SP-NCTL test is not appropriate for testing textured surfaces.  For THDEP geomembrane, test should be conducted on smooth edges of textured rolls or on smooth sheets made from the same formulation as being used for the textured sheet material.

- The manufacturer has the option to select either one of the OIT methods listed to evaluate the antioxidant content in the geomembrane.

- It is also recommended to evaluate samples at 30 and 60 days to compare with the 90 day response.

- The condition of the test should be 20 hr. UV cycle at 75oC followed by 4 hr. condensation at 60oC.

- UV resistance is based on the percent retained value regardless of the original HP-OIT value

The surfaces shall not have striations, pinholes or bubbles.

The geomembrane shall be supplied as rolls with labels on each roll which shall identify the thickness of material, the length and width of the roll, batch and roll numbers, and name of manufacturer.

2.03	RELATED MATERIALS:

- Resin used for fusion joining sheets, and sheet to pipe at geomembrane penetrations shall be HDPE produced from the same type of resins used in sheet production.  Physical properties shall be the same as those of the resin used in manufacturing of the THDPE or HDPE geomembrane.  The resin shall be colored black by the addition of carbon black.

All seams shall demonstrate a Film Tearing Bond (FTB) in peel and shear.  The field seams shall meet the following specifications:

Seam                                   ASTM Test                                           	Performance

Property                              Method                                                 	Requirements

HDPE	THDPE

Shear Strength                     D 4437                                   20 kN/m          20 kN/m

Peel Strength                       D 4437                                   15 kN/m           15 kN/m

  - See Sections 3.03 G and 3.03 I for test seam and field seam testing requirements.

  - Acceptable field seaming methods are hot shoe fusion welding and extrusion welding.

2.04	INTERFACE FRICTION OF SOIL AND GEOSYNTHETIC:

- Contractor's soil testing firm shall conduct tests to determine the interface resistance between the THDPE geomembrane with both the subgrade and cover materials in accordance with ASTM D 5321.

A minimum of one set of tests shall be performed for each type of soil used in the subgrade layer immediately beneath the liner.  Test results shall be submitted at least two weeks prior to placement of the geomembrane over the prepared subgrade surface.

A minimum of one set of tests for cover materials shall be performed.  Test results shall be submitted at least two weeks prior to placement of the cover soil.

Direct shear test shall be performed by an approved laboratory.  Soil specimens shall be prepared in accordance with ASTM D 5321 and compacted to 90% maximum dry density (ASTM D 1557) within a range in moisture of 2 to 3 percent wet of optimum.  The prepared soil samples shall be saturated in water for a minimum of 24 hours prior to testing.  The geomembrane shall be installed on top of the saturated soil sample.

The direct shear test shall be performed for two conditions:

  - Unconsolidate Undrained Conditions:  Apply the shear force to the traveling container at a constant rate ranging from 1 to 5 mm/min.  Record the shear force for at least 50 mm of total horizontal displacement.

  - Consolidated Drained Conditions:  Apply the shear force using a constant rate not greater than 0.04 mm/min.  Record the shear force for at least 50 mm of total horizontal displacement.

  - For each of the above conditions a set of three tests shall be performed at confining pressures of 7, 14 and 21 kPa.

Test results shall include peak and post-peak (at 15 to 20 percent strain) values for the interface friction angles.

The minimum peak and post-peak interface friction angles between each soil and the THDPE geomembrane shall be 27 and 23 degrees, respectively.

PART 3 - EXECUTION

3.01	TRANSPORTATION:

- Transportation is the responsibility of the Contractor.

3.02	DELIVERY AND ON-SITE STORAGE:

- Off-loading and storage is the responsibility of the Contractor.

- Off-loading shall only take place in the presence of the Engineer.

- The Contractor shall be responsible for replacing any material damaged during off-loading at no expense to the Owner.

- The material shall be kept free of all materials, debris, and solvent compounds that may adversely affect the performance of the cap.

- The rolls shall be stored on a prepared, firm surface (not wooden pallets) and shall not be stacked more than two rolls high.

- Vehicle traffic shall be prohibited from traveling on the newly installed geomembrane system.

3.03	INSTALLATION:

- Installation of the geomembrane shall be done in the presence of the Engineer.

- Subgrade surfaces and embankment walls to be smooth and free of all sharp objects or debris of any kind.  The Contractor to certify in writing that the surface on which the geomembrane is to be installed is acceptable.

- Geomembrane sheets shall be laid out and installed by qualified technicians in accordance with the approved Panel Layout Plan.  Sheets shall be placed in order to minimize the number and length of field joints.  Seams shall be orientated parallel to the line of maximum slope i.e. down the slope, not across.  No seams shall be closer than 1.5 m from the toe of the slope.  Seaming of sheets perpendicular to the line of maximum slope in the area above the top of slope shall be no closer than 3 m. from the top of slope.  Seams shall be overlapped in the downslope direction, like roof shingles.  Seams shall be aligned to prevent the least possible number of wrinkles and "fishmouths".  If a fishmouth or wrinkle is found, it shall be relieved, capped, and vacuum tested.  Geomembrane layout and placement shall be consistent with proper methods for geomembrane installation.

- Field joints shall be made by overlapping adjacent sheets.

- A double wedge seam shall be used wherever possible.  An extrusion weld seam will be used wherever construction of a double wedge seam is impossible.

- Seaming procedures using the extrusion process:

  - The overlapping of sheets shall be a minimum of 10 cm and a minimum pressure exerted during the fusion welding process shall be 14 kPa

  - All geomembrane sheeting shall be welded together by means of a homogeneous overlap extrusion fusion process that provides continuous dynamic integration of the extrudate bead with the geomembrane material.  The composition of the extrudate shall be identical to the geomembrane material.

  - The welding equipment used shall be capable of continuously monitoring and controlling the temperature of the extrudate and the zone of contact where the machine is actually fusing the geomembrane material so as to ensure changes in the environmental conditions will not affect the integrity of the weld.

- Seaming procedures using a hot shoe (double wedge) welder:

  - Overlap the two sheets of the geomembrane a minimum of 10 cm.  Surfaces to be seamed should be prepared as required by manufacturers.  The two sheets shall be straightened to keep the seamed edges smooth and wrinkle free.

  - The temperature exerted by the welding machine used to join the cap sheets shall be between 200oC and 370oC, with the exact temperature being determined by the Contractor's installation supervisor on the day of installation.

  - If additional material must be introduced during the field seaming procedure, it shall be either smooth or textured as appropriate of the same quality and physical properties of the geomembrane material.  No other material than THDPE or HDPE shall be used during the joining of geomembrane sheets.

  - The total width of the fusion seam(s) shall be a minimum of 3.5 cm.

  - The fusion seam shall produce an appropriate scrim size to ensure ease of determining field seam adequacy by installation supervisor in the field.

- Test Seams:

  - Test seams shall be performed prior to field seaming each morning and afternoon.  Test seams shall be labeled with date, time, machine I.D. number, seaming temperature, and ambient air temperature.

  - The test seam samples shall be a minimum of 3 m long for hot shoe welding and 1 meter long for extrusion welding with the seam centered lengthwise.  The Contractor shall cut specimens 2.5 cm wide from each opposite end of the test seam.  The Contractor will use a tensiometer to test these specimens for shear (ASTM D 4437) and peel (ASTM D 4437).  For test seams, a break through the weld or at the weld-sheet interface shall be considered a failure in both seam strength (shear) and peel strength.  If a test seam fails, adjustments shall be made and deficiencies corrected until two consecutive successful test seams are achieved.

  - A minimum of 30 cm of each test seam will be given to and becomes the property of the Engineer for verification of seams by an Independent testing agency.

- Non-Destructive Seam Testing: All testing to be performed in the presence of the Engineer.  The Contractor shall non-destructively test all field seams over their entire length, utilizing the following methods:

  - Vacuum Box Testing:

    - Carefully trim away excess sheet overlap (single wedge fusion seam).

    - Check vacuum box for leaks.

    - Activate the vacuum pump and reduce the tank pressure to approximately 35 kPa.

    - Wet a strip of the geomembrane just larger than the vacuum box with a soapy solution.

    - Place the box over the wetted area and compress.

    - Close the bleed valve and open the vacuum valve.

    - Ensure that a tight seal has been created.

    - Examine the geomembrane, for a minimum of 15 seconds, for the presence of soap bubbles.

    - If no bubbles appear after 15 seconds, close the vacuum valve and open the bleed valve, move the box over the next adjoining area with a minimum of 7.5 cm overlap and repeat the process.

    - All areas where soap bubbles appeared shall be marked, repaired, and retested.

  - Air Pressure Testing (For Double Fusion Seams):

The following procedures are only applicable to seaming processes that produce a double seam with an enclosed space:

    - Seal both ends of the seam to be tested.

    - Insert the pressure feed device (needle) into the enclosed space created by double wedge fusion weld.

    - Inflate the test channel to a pressure between 170 and 200 kPa, close valve, and observe initial pressure after a minimum of 2 minutes.

    - Observe and record the air pressure 5 minutes after the initial pressure setting is sustained.

    - If loss of pressure exceeds 21 kPa, or pressure does not stabilize, locate faulty area, repair and retest.

    - Remove the pressure feed device and seal.

- Destructive Seam Testing:

  - The Contractor shall provide the Engineer with a minimum of one random weld sample from the installed seams at a minimum frequency of one every 1500 m of weld.  Sampling times and locations shall be determined by the Engineer.  The Engineer must witness the obtainment of all field test samples and the Contractor shall mark all samples with their location, roll, and seam number.  The Contractor shall also record in written form the date, time, location, roll seam number, ambient temperatures, and pass or fail description.  A copy of the information must be attached to each sample portion.  All holes in the geomembrane as a result of obtaining seam samples shall be immediately repaired, with all patches being vacuum tested.

  - Samples shall be approximately 30 cm wide by 60 cm long with the seam centered lengthwise.  The sample shall be cut in half with one piece given to the Engineer and the other to the Contractor.  The Contractor shall cut his sample into ten - 2.5 cm wide pieces.  Five shall be tested for shear strength and five shall be tested for peel strength.  Testing procedures shall be ASTM D 4437 for shear and peel, as modified in Appendix A of NSF 54.  At least four of the five tests for each type of test shall exhibit a film tear bond.  The Engineer will retain his sample for independent laboratory determination of seam strength.  90 cm. long samples may be taken if the Contractor would like a 30 cm. section for his records.

- Procedures for Destructive Test Failure:

The following procedures shall be followed by the Contractor wherever a seam taken destructively fails the field seam test:

  - Reconstruct the seam between the failed location and any passed test location along the seam.

  - Retrace the weld path to an intermediate location (minimum of 3 m in each direction) agreed to between the Contractor and Engineer, and take samples for additional destructive field seam tests.  If this test passes then the seam shall be cap stripped between that location and the original failed location.  If the test fails, then the process shall be repeated.

  - After reseaming or placement of a cap strip within the reseamed area, all seams shall be vacuum tested and additional destructive field tests may be taken at the Engineer's discretion.  If test (vacuum or destructive) results are not acceptable, this process shall be repeated until the area reseamed is judged satisfactory by the Engineer.

- Penetration Procedures:

  - All geomembrane penetrations shall be sealed with an extruded hand welder.  This hand welder shall heat both material and a hot strip of THDPE or HDPE as appropriate shall be introduced to complete the sealing process.  No other material than THDPE or HDPE (as appropriate) of the same quality and grade of the geomembrane material shall be used in the geomembrane penetration sealing process.

- Patching Procedures:

  - Patching of holes , which may occur during installation, shall be sealed with the same THDPE or HDPE (as appropriate) material as the geomembrane sheets and extruded hand welder.  Prior to patching, the area shall be cleaned of all dirt, dust or other foreign material and heated to the proper temperature.

  - Small holes may be repaired by applying a cap of extrusion weld.  If the hole is larger than 6 mm., it shall be patched.

  - Tears shall be repaired by patching.  Sharp ends of tears shall be rounded out before patching.

  - Patches shall be oval in shape, of the same material and thickness of the geomembrane, and extend a minimum of 15 cm beyond all areas of the hole.  Patches shall be applied using methods recommended by the geomembrane manufacturer.

3.04	FINAL WALK OVER AND ACCEPTANCE:

- Before placement of any cover materials , the completed geomembrane shall receive a final joint walk over by the Engineer and Contractor to visually search for any undetected holes, defects, or other faults which may adversely affect the performance of the geomembrane.

- Contractor to certify in writing upon completion of Final Walk Over as to concurrence and satisfaction of event and any remedial action taken as a result of defects discovered.

3.05	PLACEMENT OF GEOMEMBRANE PROTECTIVE  LAYER:

- After the placement of the geomembrane, a protective  layer shall be placed over the geomembrane.  This layer shall consist of a mud coat or portion of the concrete slab layer on the bottom of the drying beds.  Work associated with placing this layer shall be accomplished with  low ground pressure equipment, pumpeding, to avoid damaging the geomembrane.  Equipment shall not travel over the exposed geomembrane.  On the drying bed slopes, the soil cement layer shall be place with small size and low pressure machines to avoid geomembrane damage.

- Contractor's Geomembrane Installation Supervisor shall remain onsite after the final work to advise on procedures and monitor throughout the period of placement of select cover materials.

- Contractor shall not use construction equipment that will result in slope failure.  The maximum construction loads that may be imposed on the geomembrane or the overlaying materials shall be determined and established by the Contractor's independent testing company.

The term "Contractor" stands for both men and women.